## Summary Overview
|  | STP Routine cyclical tasks 23-24 |  |  |  | STP M & E - Weekly PPM | STP M & E - Weekly PPM | STP M & E - Weekly PPM | STP M & E - Weekly PPM | STP M & E - Weekly PPM | STP M & E - Weekly PPM | STP M & E - Weekly PPM | STP M & E - Weekly PPM | STP M & E - Weekly PPM | STP M & E - Weekly PPM | STP M & E - Weekly PPM | STP M & E - Weekly PPM | STP M & E Monthly | STP M & E Monthly | STP M & E Monthly | STP M & E Monthly | STP M & E Monthly | STP M & E Monthly | STP M & E Monthly | STP M & E Monthly | STP M & E Monthly | STP M & E Monthly | STP M & E Monthly | STP M & E Monthly | STP M & E Bi Monthly | STP M & E Quarterly | STP M & E Quarterly | STP M & E Quarterly | STP M & E Quarterly | STP M & E Quarterly | STP M & E Quarterly | STP M & E Quarterly | STP M & E Quarterly | STP M & E Quarterly | STP M & E Quarterly | STP M & E Quarterly | STP M & E Quarterly | STP M & E 6 Monthly (Twice per annum) | STP M & E 6 Monthly (Twice per annum) | STP M & E 6 Monthly (Twice per annum) | STP M & E 6 Monthly (Twice per annum) | STP M & E 6 Monthly (Twice per annum) | STP M & E 6 Monthly (Twice per annum) | STP M & E 6 Monthly (Twice per annum) | STP M & E 6 Monthly (Twice per annum) | STP M & E 6 Monthly (Twice per annum) | STP M & E 6 Monthly (Twice per annum) | STP M & E 6 Monthly (Twice per annum) | STP M & E 6 Monthly (Twice per annum) | STP M & E Annual | STP M & E Annual | STP M & E Annual | STP M & E Annual | STP M & E Annual | STP M & E Annual | STP M & E Annual | STP M & E Annual | STP M & E Annual | STP M & E Annual | STP M & E Annual | STP M & E Annual | STP Sample | STP Sample | STP Sample | STP Sample | STP Sample | STP Sample | STP Sample | STP Sample | STP Sample | STP Sample | STP Sample | STP Sample | STP Desludge Primary Tank | STP Desludge Primary Tank | STP Desludge Primary Tank | STP Desludge Primary Tank | STP Desludge Primary Tank | STP Desludge Primary Tank | STP Desludge Primary Tank | STP Desludge Primary Tank | STP Desludge Primary Tank | STP Desludge Primary Tank | STP Desludge Primary Tank | STP Desludge Primary Tank | STP Desludge Final Tank | STP Desludge Final Tank | STP Desludge Final Tank | STP Desludge Final Tank | STP Desludge Final Tank | STP Desludge Final Tank | STP Desludge Final Tank | STP Desludge Final Tank | STP Desludge Final Tank | STP Desludge Final Tank | STP Desludge Final Tank | STP Desludge Final Tank | Pumping stations M&E Monthly | Pumping stations M&E Monthly | Pumping stations M&E Monthly | Pumping stations M&E Monthly | Pumping stations M&E Monthly | Pumping stations M&E Monthly | Pumping stations M&E Monthly | Pumping stations M&E Monthly | Pumping stations M&E Monthly | Pumping stations M&E Monthly | Pumping stations M&E Monthly | Pumping stations M&E Monthly | Pumping stations M&E Quarterly | Pumping stations M&E Quarterly | Pumping stations M&E Quarterly | Pumping stations M&E Quarterly | Pumping stations M&E Quarterly | Pumping stations M&E Quarterly | Pumping stations M&E Quarterly | Pumping stations M&E Quarterly | Pumping stations M&E Quarterly | Pumping stations M&E Quarterly | Pumping stations M&E Quarterly | Pumping stations M&E Quarterly | Pumping stations M&E Six Monhtly | Pumping stations M&E Six Monhtly | Pumping stations M&E Six Monhtly | Pumping stations M&E Six Monhtly | Pumping stations M&E Six Monhtly | Pumping stations M&E Six Monhtly | Pumping stations M&E Six Monhtly | Pumping stations M&E Six Monhtly | Pumping stations M&E Six Monhtly | Pumping stations M&E Six Monhtly | Pumping stations M&E Six Monhtly | Pumping stations M&E Six Monhtly | Pumping stations M&E Annual | Pumping stations M&E Annual | Pumping stations M&E Annual | Pumping stations M&E Annual | Pumping stations M&E Annual | Pumping stations M&E Annual | Pumping stations M&E Annual | Pumping stations M&E Annual | Pumping stations M&E Annual | Pumping stations M&E Annual | Pumping stations M&E Annual | Pumping stations M&E Annual | Septic tank empties | Septic tank empties | Septic tank empties | Septic tank empties | Septic tank empties | Septic tank empties | Septic tank empties | Septic tank empties | Septic tank empties | Septic tank empties | Septic tank empties | Septic tank empties
[6 empty] | STP M & E - Weekly PPM | [11 empty] | STP M & E Monthly | [12 empty] | STP M & E Quarterly | [11 empty] | STP M & E 6 Monthly (Twice per annum) | [11 empty] | STP M & E Annual | [11 empty] | STP Sample | [11 empty] | STP Desludge Primary Tank | [11 empty] | STP Desludge Final Tank | [11 empty] | Pumping stations M&E Monthly | [11 empty] | Pumping stations M&E Quarterly | [11 empty] | Pumping stations M&E Six Monhtly | [11 empty] | Pumping stations M&E Annual | [11 empty] | Septic tank empties
Lot | Region | Address | STP | Pumps | Septic | Apr | May | Jun | Jul | Aug | Sept | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sept | Oct | Nov | Dec | Jan | Feb | Mar | Apr | Apr | May | Jun | Jul | Aug | Sept | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sept | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sept | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sept | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sept | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sept | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sept | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sept | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sept | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sept | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sept | Oct | Nov | Dec | Jan | Feb | Mar
1 | North Hampshire | Verlynch Cottages | √ | [14 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  |  |  | √ |  |  | √ |  |  | √ |  |  | √ |  |  | √ | [5 empty] | √ | [11 empty] | √ |  |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  | √ |  | √ |  | √ |  | √ |  | √
1 | North Hampshire | School Lane | √ | [14 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | [37 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  |  | √ |  |  | √ |  |  | √ |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
1 | North Hampshire | Brookside Cottages | √ | [14 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  |  |  | √ |  |  | √ |  |  | √ |  |  | √ |  |  | √ | [5 empty] | √ | [11 empty] | √ |  |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  | √ | √ | √ |  | √ |  | √ |  | √ | √ | √ |  | √ | √ | √ |  | √ |  | √ |  | √
1 | North Hampshire | Bulpits Hill | √ | [14 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  |  |  | √ |  |  | √ |  |  | √ |  |  | √ |  |  | √ | [5 empty] | √ | [11 empty] | √ |  |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  |  | √ |  |  | √ |  |  | √
1 | North Hampshire | Pound View | √ | [14 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  |  |  | √ |  |  | √ |  |  | √ |  |  | √ |  |  | √ | [5 empty] | √ | [11 empty] | √ |  |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  |  | √ |  |  | √ |  |  | √
1 | North Hampshire | The Close | √ | [14 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  |  |  | √ |  |  | √ |  |  | √ |  |  | √ |  |  | √ | [5 empty] | √ | [11 empty] | √ |  |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  |  |  | √ |  |  |  | √ |  |  |  | √ |  |  |  | √ |  |  |  | √
1 | North Hampshire | Hillplace | √ | [26 empty] | √ |  |  | √ |  |  | √ |  |  | √ |  |  | √ |  |  | √ | [5 empty] | √ | [11 empty] | √ |  |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  | √ | √ | √ |  | √ |  | √ |  | √
1 | North Hampshire | Yew Tree Walk |  | √ | [112 empty] | √ |  |  | √ |  |  | √ |  |  | √ | [5 empty] | √ | [5 empty] | √ | [11 empty] | √
1 | North Hampshire | Lion Oak Court |  | √ | [112 empty] | √ |  |  | √ |  |  | √ |  |  | √ | [5 empty] | √ | [5 empty] | √ | [11 empty] | √
1 | North Hampshire | Abbotts Ann Down |  |  | √ | [150 empty] | √ | [5 empty] | √
1 | North Hampshire | Stoney Drove |  |  | √ | [145 empty] | √ | [5 empty] | √
1 | North Hampshire | Aylwards Way |  |  | √ | [146 empty] | √ | [5 empty] | √
1 | North Hampshire | Cottage Road |  |  | √ | [147 empty] | √ | [5 empty] | √
1 | North Hampshire | Cottage Road |  |  | √ | [147 empty] | √ | [5 empty] | √
1 | North Hampshire | Cottage Road |  |  | √ | [147 empty] | √ | [5 empty] | √
1 | North Hampshire | Fifehead Cottages |  |  | √ | [145 empty] | √ | [5 empty] | √
1 | North Hampshire | Dean Terrace |  |  | √ | [146 empty] | √ |  |  | √ |  |  | √ |  |  | √
1 | North Hampshire | Hatchbury Lane |  |  | √ | [148 empty] | √ | [5 empty] | √
1 | North Hampshire | Hillside Cottages |  |  | √ | [148 empty] | √ | [5 empty] | √
1 | North Hampshire | Upper Chute |  |  | √ | [146 empty] | √ |  |  | √ |  |  | √ |  |  | √
2 | South Hampshire | Stevens Drove | √ | √ | [13 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  |  |  | √ |  |  | √ |  |  | √ |  |  | √ |  |  | √ | [5 empty] | √ | [11 empty] | √ |  |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  | √ |  |  | √ |  |  | √ |  |  | √ |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
2 | South Hampshire | Manor Road | √ | [14 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | [37 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  |  |  | √ |  |  |  | √ |  |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
2 | South Hampshire | Dean Road | √ | [14 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | [37 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  |  |  | √ |  |  |  | √ |  |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
2 | South Hampshire | East Dean Road | √ | [14 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  |  |  | √ |  |  | √ |  |  | √ |  |  | √ |  |  | √ | [5 empty] | √ | [11 empty] | √ |  |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  | √ |  |  | √ |  |  | √ |  |  | √
2 | South Hampshire | Carters Clay Road | √ | [14 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  |  |  | √ |  |  | √ |  |  | √ |  |  | √ |  |  | √ | [5 empty] | √ | [11 empty] | √ |  |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  |  |  | √ |  |  |  | √
2 | South Hampshire | Lymer Villas | √ | [14 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  |  |  | √ |  |  | √ |  |  | √ |  |  | √ |  |  | √ | [5 empty] | √ | [11 empty] | √ |  |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  |  | √ |  |  | √ |  |  | √
2 | South Hampshire | Green Pond Lane | √ |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | [15 empty] | √ |  |  | √ |  |  | √ |  |  | √ | [24 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
2 | South Hampshire | Glebe Meadow | √ | [14 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  |  |  | √ |  |  | √ |  |  | √ |  |  | √ |  |  | √ | [5 empty] | √ | [11 empty] | √ |  |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  | √ |  | √ |  | √ |  | √ |  | √ |  | √ |  | √ |  | √ |  | √ |  | √ |  | √
2 | South Hampshire | Oval Road | √ | [14 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  |  |  | √ |  |  | √ |  |  | √ |  |  | √ |  |  | √ | [5 empty] | √ | [11 empty] | √ |  |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  | √ | √ |  | √ |  | √ |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
2 | South Hampshire | Butlers Close | √ | [14 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  |  |  | √ |  |  | √ |  |  | √ |  |  | √ |  |  | √ | [5 empty] | √ | [11 empty] | √ |  |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  | √ |  | √ |  | √ |  | √ |  | √ |  |  |  |  | √ |  |  |  | √ |  |  |  | √
2 | South Hampshire | Pragnells Cottages | √ | [14 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  |  |  | √ |  |  | √ |  |  | √ |  |  | √ |  |  | √ | [5 empty] | √ | [11 empty] | √ |  |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  | √ |  |  | √ |  |  | √ |  |  | √
2 | South Hampshire | Cowleas Cottages | √ | √ |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  |  |  | √ |  |  | √ |  |  | √ |  |  | √ |  |  | √ | [5 empty] | √ | [11 empty] | √ |  |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  | √ |  | √ |  | √ |  | √ |  | √ |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | [14 empty] | √ |  |  | √ |  |  | √ |  |  | √ | [5 empty] | √ | [5 empty] | √ | [11 empty] | √
2 | South Hampshire | Eagle Court |  | √ | [112 empty] | √ |  |  | √ |  |  | √ |  |  | √ | [5 empty] | √ | [5 empty] | √ | [11 empty] | √
2 | South Hampshire | Hillside Cottages |  |  | √ | [148 empty] | √ | [5 empty] | √
2 | South Hampshire | Rectory Hill Cottages + Newlands |  |  | √ | [145 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
2 | South Hampshire | Up Somborne |  |  | √ | [151 empty] | √
3 | East Dorset | Burgess Fields | √ | [14 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | [37 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
3 | East Dorset | Tillingbourne Court |  | √ | [112 empty] | √ |  |  | √ |  |  | √ |  |  | √ | [5 empty] | √ | [5 empty] | √ | [11 empty] | √
3 | East Dorset | Hibberd Court |  | √ | [112 empty] | √ |  |  | √ |  |  | √ |  |  | √ | [5 empty] | √ | [5 empty] | √ | [11 empty] | √
3 | East Dorset | Cunningham Close |  | √ | [112 empty] | √ |  |  | √ |  |  | √ |  |  | √ | [5 empty] | √ | [5 empty] | √ | [11 empty] | √
3 | East Dorset | Chapter House |  | √ | [112 empty] | √ |  |  | √ |  |  | √ |  |  | √ | [5 empty] | √ | [5 empty] | √ | [11 empty] | √
3 | East Dorset | Jubilee Court |  | √ | [112 empty] | √ |  |  | √ |  |  | √ |  |  | √ | [5 empty] | √ | [5 empty] | √ | [11 empty] | √
3 | East Dorset | Hardy Close |  | √ | [112 empty] | √ |  |  | √ |  |  | √ |  |  | √ | [5 empty] | √ | [5 empty] | √ | [11 empty] | √
3 | East Dorset | Hawthorne Common |  |  | √ | [148 empty] | √
4 | West Dorset | Colehill Drove | √ | [29 empty] | √ |  |  | √ |  |  | √ |  |  | √ |  |  | √ | [5 empty] | √ | [15 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  |  | √ |  |  | √ |  |  | √ |  |  | √
4 | West Dorset | Newton Hill | √ | [14 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | [37 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  |  | √ |  |  | √ |  |  | √ |  |  | √
4 | West Dorset | Shaggs Cottages | √ | [14 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | [37 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  |  | √ |  |  | √ |  |  | √ |  |  | √
4 | West Dorset | Blackmanston | √ | [29 empty] | √ |  |  | √ |  |  | √ |  |  | √ |  |  | √ | [5 empty] | √ | [11 empty] | √ |  |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  |  | √ |  |  | √ |  |  | √ |  |  | √
4 | West Dorset | Woodsford Lane | √ | [29 empty] | √ |  |  | √ |  |  | √ |  |  | √ |  |  | √ | [5 empty] | √ | [11 empty] | √ |  |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  |  | √ |  |  | √ |  |  | √ |  |  | √
4 | West Dorset | Organford | √ | [29 empty] | √ |  |  | √ |  |  | √ |  |  | √ |  |  | √ | [5 empty] | √ | [15 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  |  | √ |  |  | √ |  |  | √ |  |  | √
4 | West Dorset | Middlehill cottages |  | √ | [112 empty] | √ |  |  | √ |  |  | √ |  |  | √ | [5 empty] | √ | [5 empty] | √ | [11 empty] | √
5 | Devon & Cornwall | Ford Close | √ | [14 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | [37 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  |  | √ |  |  | √ |  |  | √ |  |  | √
5 | Devon & Cornwall | Squirrel Close |  | √ | [112 empty] | √ |  |  | √ |  |  | √ |  |  | √ | [5 empty] | √ | [5 empty] | √ | [11 empty] | √
5 | Devon & Cornwall | Congdons Orchard |  | √ | [112 empty] | √ |  |  | √ |  |  | √ |  |  | √ | [5 empty] | √ | [5 empty] | √ | [11 empty] | √
5 | Devon & Cornwall | Miller Way |  | √ | [112 empty] | √ |  |  | √ |  |  | √ |  |  | √ | [5 empty] | √ | [5 empty] | √ | [11 empty] | √
5 | Devon & Cornwall | Collacott Close |  | √ | [112 empty] | √ |  |  | √ |  |  | √ |  |  | √ | [5 empty] | √ | [5 empty] | √ | [11 empty] | √
6 | Somerset | Church View | √ | [29 empty] | √ |  |  | √ |  |  | √ |  |  | √ |  |  | √ | [5 empty] | √ | [11 empty] | √ |  |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  | √ |  |  | √ |  |  | √ |  |  | √
6 | Somerset | Pilton Road | √ | [29 empty] | √ |  |  | √ |  |  | √ |  |  | √ |  |  | √ | [5 empty] | √ | [11 empty] | √ |  |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  | √ |  |  | √ |  |  | √ |  |  | √
6 | Somerset | Fosse Cottages | √ | [29 empty] | √ |  |  | √ |  |  | √ |  |  | √ |  |  | √ | [5 empty] | √ | [11 empty] | √ |  |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  | √ |  |  | √ |  |  | √ |  |  | √
6 | Somerset | Keywards House | √ | [14 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  |  |  | √ |  |  | √ |  |  | √ |  |  | √ |  |  | √ | [5 empty] | √ | [11 empty] | √ |  |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  | √ |  |  | √ |  |  | √ |  |  | √
6 | Somerset | The Leaze | √ | [29 empty] | √ |  |  | √ |  |  | √ |  |  | √ |  |  | √ | [5 empty] | √ | [11 empty] | √ |  |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  | √ |  |  | √ |  |  | √ |  |  | √
6 | Somerset | Zion Hill | √ | [14 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  |  |  | √ |  |  | √ |  |  | √ |  |  | √ |  |  | √ | [5 empty] | √ | [11 empty] | √ |  |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  | √ |  |  | √ |  |  | √ |  |  | √
7 | Wiltshire | Kennet Valley Mews | √ | [29 empty] | √ |  |  | √ |  |  | √ |  |  | √ |  |  | √ | [5 empty] | √ | [11 empty] | √ |  |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  | √ |  |  | √ |  |  | √ |  |  | √
7 | Wiltshire | Burbage Road |  |  | √ | [146 empty] | √ |  |  | √ |  |  | √ |  |  | √
7 | Wiltshire | The Pelch |  |  | √ | [146 empty] | √ |  |  | √ |  |  | √ |  |  | √
7 | Wiltshire | Chandlers Lane |  |  | √ | [146 empty] | √ |  |  | √ |  |  | √ |  |  | √

## Verlynch Cottages
| STP Hampshire - Maintenance Item Description, Verlynch Cottages | Quantity | Frequency | Apr | May | June | Jul | Aug | Sept | Oct | Nov | Dec | Jan | Feb | Mar
Item | Maintenance works including:
1 | unlock and enter and set telemetry “Engineer on Site” switch. Check security of gates and fences. Check for rodent infestation. Check warning signs, condition of manhole/access covers and frames, ladders, step irons, handrailing, steps and working platforms, including: | 12 | Monthly | bar: Apr to Mar
2 | Lift access covers, inspect and clean distributor to ensure arms are free of debris and effluent is being evenly distributed. Check for surface ponding and report. Clean filter arm rotation sensor. Replace covers. | 12 | Monthly | bar: Apr to Mar
3 | Lift access covers and clean channels, weirs, scum boards, and dip pipes of inlet chamber and primary tank by jet washing. Clean high level alarm float of rags and other debris. Replace covers. | 12 | Monthly | bar: Apr to Mar
4 | Clean sample/level control chamber walls and floor by jet washing. Check operation of level control device. | 4 | Qtr. | bar: June; Sept
5 | Clean all manholes and collection pits within the site by jet washing, including channels, walls, benching and frame rebates. Clean covers and clear lifting eyes of debris and re-fit. | 4 | Qtr. | bar: June; Sept
6 | Tidy site. | 12 | Monthly | bar: Apr to Mar
7 | Visual check on effluent. | 12 | Monthly | bar: Apr to Mar
8 | Clean, check operation and oil all padlocks on site. | 12 | Monthly | bar: Apr to Mar
Control Kiosk (All equipment must be isolated before any maintenance work is carried out)
9 | Inspect cables and fittings. Check heater and thermostat setting. Check operation of indicators, lamps, lights and security of earthing straps. | 12 | Monthly | bar: Apr to Mar
10 | Check/re-set overloads. | 12 | Monthly | bar: Apr to Mar
11 | Check reed bed distribution area and clear any accumulation of weeds and debris. | 12 | Monthly | bar: Apr to Mar
12 | Check operation of break tank valve, ball valve and drain down. | 4 | Qtr. | bar: June; Sept; Dec; Mar
13 | Check filter arms for ‘soundness’. Check straining wires/adjusters and rectify any faults with distributor mechanism. Grease/oil moving parts requiring lubrication. | 4 | Qtr. | bar: June; Sept; Dec; Mar
14 | Cut the grass and weeds to keep them short and prevent seeding. Trim back hedgerows. Remove arisings to authorised tip. | 4 | Qtr. | bar: June; Sept; Dec; Mar
15 | Carry out thorough clean of the control kiosk, remove cobwebs and dirt and wipe down exterior. | 4 | Qtr. | bar: June; Sept; Dec; Mar
16 | Inspect and clean inlet risers by brushing. | 2 | Biannual | bar: June; Dec
17 | Raise level control device and flood reed bed for weed and pest control. (Spring and Autumn) | 2 | Biannual | bar: June; Dec
18 | Read and record the electricity and water meters (end of June and December) | 2 | Biannual | bar: June; Dec
19 | Rod inlet distribution pipe and perforated outlet pipe. | 1 | Annual | bar: Dec
20 | After leaf fall in autumn collect all leaves from the site and dispose to authorised tip. Check overhang of trees and report any encroachment over treatment units. | 1 | Annual | bar: Dec
21 | Check for earth continuity. | 1 | Annual | bar: Dec

## School Lane
| STP Hampshire - Maintenance Item Description School Lane | Quantity | Frequency | Apr | May | June | Jul | Aug | Sept | Oct | Nov | Dec | Jan | Feb | Mar
Item | Maintenance works including:
| Unlock, enter and set telemetry “Engineer on Site” switch. Check security of gates and fences. Check for rodent infestation. Check warning signs, condition of manhole/access covers and frames, ladders, step irons, handrailing, steps and working platforms. | 12 | Monthly | bar: Apr to Mar
| Lift access cover and clean high level alarm float of rags and other debris. Replace cover. | 12 | Monthly | bar: Apr to Mar
| Tidy site. | 12 | Monthly | bar: Apr to Mar
| Visual check on effluent. | 12 | Monthly | bar: Apr to Mar
| Ensure septic tank inlets are clear of blockages/solids build-up by jet washing. De-sludge SAF cells (3 No.) and Final Tank as specified. Re-check inlets during and following de-sludging to ensure free flow into septic tanks is maintained. | 12 | Monthly | bar: Apr to Mar
Blower/Control Kiosk
(All equipment must be isolated before any maintenance work is carried out)
| Inspect cables and fittings. Check heater and thermostat setting. Check operation of indicators, lamps, light and security of earthing straps. | 12 | Monthly | bar: Apr to Mar
| Check/reset overloads as specified. | 12 | Monthly | bar: Apr to Mar
| Check reading on pressure gauge as specified. | 12 | Monthly | bar: Apr to Mar
| Check pressure relief for escaping air as specified. | 12 | Monthly | bar: Apr to Mar
| Inspect Copa sac installation and change bag when blinded or one third full and dispose to authorised tip. Clean frame and fit new bag. | 12 | Monthly | bar: Apr to Mar
| Inspect/adjust air pattern as specified. | 12 | Monthly | bar: Apr to Mar
| Check operation of break tank valve, ball valve and drain down. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Inspect and clean sample/flow meter chamber by jet washing. Remove accumulated debris behind ‘V’ notch weir. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Clean all manholes and collection pits within the site by jet washing, including channels, walls benching and frame rebates, clean covers and clear lifting eyes and re-fit | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Clean, check operation and oil all padlocks on site. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Carry out thorough clean of the control kiosk, remove cobwebs and dirt and wipe down exterior. | 4 | Qtr. | bar: June; Sept; Dec; Mar
Access Track
| Cut grass and weed on access track only to keep it short and prevent seeding four times/annum (April, June, August and September) Remove cuttings to authorised tip. Strim around fence lines, gates. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Clean inside fan hood and blower surfaces to prevent over heating and inspect blower components (impeller, motor casing etc). | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Carry out thorough clean of the control kiosk, remove cobwebs and dirt and wipe down exterior. | 4 | Qtr. | bar: June; Sept; Dec; Mar
Sludge Pump
| Remove pump and check impeller is free from debris. Check impeller and casing etc for damage. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Check oil and replace if oil is emulsified & containing water. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Read and record the electricity and water meters (end of June and December) | 2 | Biannual | bar: June; Dec
| Clean leaves & other accumulated debris from the site, sweep paved areas and dispose of all arisings to authorised tip. | 2 | Biannual | bar: June; Dec
| Replace oxidising agent in the ‘Peacemaker’ vent stack gas filter. | 2 | Biannual | bar: June; Dec
| Change blower air filters (2 No.) as specified. | 2 | Biannual | bar: June; Dec
| Weed kill gravel and paved areas using an approved weed killer suitable for use adjacent to water courses and above aquifers. | 2 | Biannual | bar: June; Dec
| Check soakaway operation. Empty any accumulated effluent/sludge and clean by jet washing. | 1 | Annual | bar: Dec
| Check for earth continuity. | 1 | Annual | bar: Dec
| Change oil and replace plug ‘O’ rings as specified. | 1 | Annual | bar: Dec
| Check insulation resistance on all phases as specified. | 1 | Annual | bar: Dec
| Check for earth continuity. | 1 | Annual | bar: Dec
| Check earth loop impedance as specified. | 1 | Annual | bar: Dec

## Brookside Cottages
| STP HAMPSHIRE - Maintenance Item Description, Brookside Cottages | Quantity | Frequency | Apr | May | June | Jul | Aug | Sept | Oct | Nov | Dec | Jan | Feb | Mar
Item | Maintenance works including:
| Unlock, enter and set telemetry “Engineer on Site” switch. Check security of gates and fences. Check for rodent infestation. Check warning signs, condition of manhole/access covers and frames, ladders, step irons, handrailing, steps and working platforms. | 12 | Monthly | bar: Apr to Mar
| Lift access covers and clean channels, weirs, scum boards and dip pipes of inlet chamber and primary tank by jet washing. Clean high level alarm float of rags and other debris. Replace covers. | 12 | Monthly | bar: Apr to Mar
| Tidy site. | 12 | Monthly | bar: Apr to Mar
Clereflo Treatment Plant
| Check operation of the re-circulation pumps (3 No.) as specified. | 12 | Monthly | bar: Apr to Mar
| Check and confirm that there are no leaks from exposed pipework. | 12 | Monthly | bar: Apr to Mar
| Check final effluent discharge as specified. | 12 | Monthly | bar: Apr to Mar
| Control Kiosk (All equipment must be isolated before any maintenance work is carried out) | 12 | Monthly | bar: Apr to Mar
| Inspect cables and fittings. Check heater and thermostat setting. Check operation of indicators, lamps, lights and security of earthing straps. | 12 | Monthly | bar: Apr to Mar
| Check/re-set overloads. | 12 | Monthly | bar: Apr to Mar
Forward feed air lift pumps
| Empty well, clean and inspect pumps | 4 | Qtr. | bar: June; Sept; Dec; Mar
(Before carrying out the following maintenance task ensure that the power is off and the mains isolator is padlocked)
| Check for correct operation of the sludge return pump as specified. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Check operation of break tank valve, ball valve and drain down. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Inspect and clean sample chamber by jet washing. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Clean all manhole and collection pits within the site by jet washing including channels, walls, benchings and frame rebates. Clean covers and clear lifting eyes and re-fit. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Clean, check operation and oil all padlocks on site. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Carry out thorough clean of the control kiosk, remove cobwebs, dirt and wipe down exterior. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Read and record the electricity and water meters(end of June and December). | 2 | Biannual | bar: June; Dec
| Clean leaves and other accumulated debris from the site and dispose of all arisings to authorised tip. Check overhang of trees and report any encroachment over the treatment units. | 2 | Biannual | bar: June; Dec
| Check condition of seasonal discharge outfall. Clear away any accumulated debris and cut back overgrowth. | 2 | Biannual | bar: June; Dec
| Inspect and clean the re-circulation and sludge pumps as specified. | 2 | Biannual | bar: June; Dec
| Weed kill gravel areas using an approved weed killer suitable for use adjacent to watercourses and above aquifers. | 2 | Biannual | bar: June; Dec
| Check for earth continuity. | 1 | Annual | bar: Dec

## Bulpits Hill
| STP HAMPSHIRE - Maintenance Item Description, Bulpits Hill | Quantity | Frequency | Apr | May | June | Jul | Aug | Sept | Oct | Nov | Dec | Jan | Feb | Mar
Item | Maintenance works including:
Inspect treatment works, including:
| Unlock, enter and set telemetry “Engineer on Site” switch. Check security of gates and fences. Check for rodent infestation. Check warning signs, condition of manhole/access covers and frames, ladders, step irons, handrailing, steps and working platforms. | 12 | Monthly | bar: Apr to Mar
| Lift access cover and clean high level alarm float of rags and other debris. Replace cover. | 12 | Monthly | bar: Apr to Mar
| Tidy site. | 12 | Monthly | bar: Apr to Mar
| Clereflo Treatment Plant | 12 | Monthly | bar: Apr to Mar
(Before carrying out the following maintenance task ensure that the power is off and the mains isolator is padlocked)
| Check operation of the re-circulation pump as specified. | 12 | Monthly | bar: Apr to Mar
| Check and confirm that there are no leaks from exposed pipework. | 12 | Monthly | bar: Apr to Mar
| Check final effluent discharge as specified. | 12 | Monthly | bar: Apr to Mar
| Control Kiosk (All equipment must be isolated before any maintenance work is carried out) | 12 | Monthly | bar: Apr to Mar
| Inspect cables and fittings. Check heater and thermostat setting. Check operation of indicators, lamps, lights and security of earthing straps. | 12 | Monthly | bar: Apr to Mar
| Check/re-set overloads. | 12 | Monthly | bar: Apr to Mar
| Check operation of break tank valve, ball valve and drain down. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Inspect and clean sample chamber by jet washing. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Clean all manholes and collection pits within the site by jet washing including channels, walls, benching’s and frame rebates. Clean covers and clear lifting eyes and re-fit. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Clean, check operation and oil all padlocks on site. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Carry out thorough clean of the control kiosk, remove cobwebs, dirt and wipe down exterior. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Read and record the electricity and water meters (end of June and December). | 2 | Biannual | bar: June; Dec
| Clean leaves and other accumulated debris from the site and dispose of all arisings to authorised tip. Check overhang of trees and report any encroachment over the treatment units. | 2 | Biannual | bar: June; Dec
| Inspect and clean the re-circulation pump as specified. | 2 | Biannual | bar: June; Dec
| Weed kill gravel areas using an approved weed killer suitable for use adjacent to watercourses and above aquifers. | 2 | Biannual | bar: June; Dec
| Check for earth continuity. | 1 | Annual | bar: Dec

## Pound View
| STP HAMPSHIRE - Maintenance Item Description, Pound View | Quantity | Frequency | Apr | May | June | Jul | Aug | Sept | Oct | Nov | Dec | Jan | Feb | Mar
Item | Maintenance works including:
| Unlock and enter. Check security of gates and fences. Check for rodent infestation. Check warning signs, condition of manhole/access covers and frames, ladders, step irons, handrailing, steps and working platforms. | 12 | Monthly | bar: Apr to Mar
| Clean sample/level control chamber walls and floor by jet washing. Check operation of level control device. | 12 | Monthly | bar: Apr to Mar
| Clean all manholes and collection pits within the site by jet washing, including channels, walls, benching and frame rebates. Clean covers and clear lifting eyes of debris and re-fit. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Tidy site. | 12 | Monthly | bar: Apr to Mar
| Visual check on effluent. | 12 | Monthly | bar: Apr to Mar
| Check soakaway operation. Empty any accumulated effluent/sludge and clean by jet washing. | 12 | Monthly | bar: Apr to Mar
| Check reed bed distribution area and clear any accumulation of weeds and debris. | 12 | Monthly | bar: Apr to Mar
| Clean, check operation and oil all padlocks on site. | 4 | Qtr. | bar: June; Sept; Dec; Mar
Reed Bed
| Inspect and clean inlet risers by brushing. | 2 | Biannual | bar: June; Dec
| Raise level control device and flood reed bed for weed and pest control. (Spring and Autumn) | 2 | Biannual | bar: June; Dec
| After leaf fall in autumn collect all leaves from the site and dispose to authorised tip. | 1 | Annual | bar: Dec
| Weed kill shingle areas annually (July) using an approved weed killer suitable for use adjacent to watercourses and above aquifers | 2 | Biannual | bar: June; Dec
| Rod inlet distribution pipe and perforated outlet pipe. | 1 | Annual | bar: Dec

## Stevens Drove
| STP HAMPSHIRE - Maintenance Item Description, Stevens Drove | Quantity | Frequency | Apr | May | June | Jul | Aug | Sept | Oct | Nov | Dec | Jan | Feb | Mar
Item | Maintenance works including:
| Unlock, enter and set telemetry “Engineer on Site” switch. Check security of gates and fences. Check for rodent infestation. Check warning signs, condition of manhole/access covers and frames, ladders, step irons, handrailing, steps and working platforms. | 12 | Monthly | bar: Apr to Mar
| Lift access cover and clean high level alarm float of rags and other debris. Replace cover. | 12 | Monthly | bar: Apr to Mar
| Tidy site. | 12 | Monthly | bar: Apr to Mar
| Clereflo Treatment Plant | 12 | Monthly | bar: Apr to Mar
| Check operation of the re-circulation pumps (2 No.) as specified. | 12 | Monthly | bar: Apr to Mar
| Check and confirm that there are no leaks from exposed pipework. | 12 | Monthly | bar: Apr to Mar
| Check final effluent discharge as specified. | 12 | Monthly | bar: Apr to Mar
Control Kiosk (All equipment must be isolated before any maintenance work is carried out)
| Inspect cables and fittings. Check heater and thermostat setting. Check operation of indicators, lamps, lights and security of earthing straps. | 12 | Monthly | bar: Apr to Mar
| Check/re-set overloads. | 12 | Monthly | bar: Apr to Mar
Forward feed air lift pumps
| Empty well, clean and inspect pumps | 4 | Qtr. | bar: June; Sept; Dec; Mar
(Before carrying out the following maintenance task ensure that the power is off and the mains isolator is padlocked)
| Check for correct operation of the sludge return pump as specified. | 4 | Qtr. | bar: June; Sept; Dec; Mar
Off-site Pumping Station No. 1 (Unit Lift and Force Ejector
| Lift wet well cover, lift and clean floats of rags and other debris. Replace cover. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Check and clean pump by manual operation. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Check compressor oil levels and condition and top-up as required. | 4 | Qtr. | bar: June; Sept; Dec; Mar
Control Kiosk (P.S. No 1)
(All equipment must be isolated before any maintenance work is carried out)
| Inspect cables and fittings. Check heater and thermostat setting. Check operation of indicators, lamps, lights and security of earthing straps. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Check/re-set overloads. | 4 | Qtr. | bar: June; Sept; Dec; Mar
Off-site Pumping Station No. 2 (Unit Lift and Force Ejector
| Lift wet well cover, lift and clean floats of rags and other debris. Replace cover. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Check and clean pump by manual operation. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Check compressor oil levels and condition and top-up as required. | 4 | Qtr. | bar: June; Sept; Dec; Mar
Control Kiosk (P.S. No. 2)
(All equipment must be isolated before any maintenance work is carried out).
| Inspect cables and fittings. Check heater and thermostat setting. Check operation of indicators, lamps, lights and security of earthing straps. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Check/re-set overloads. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Inspect and clean sample chamber by jet washing. | 2 | Biannual | bar: June; Dec
| Clean, check operation and oil all padlocks on site. | 2 | Biannual | bar: June; Dec
| Clean all manholes and collection pits within the site by jet washing including channels, walls, benching and frame rebates. Clean covers and clear lifting eyes and re-fit. | 2 | Biannual | bar: June; Dec
| Carry out thorough clean of the control kiosk, remove cobwebs, dirt and wipe down exterior. | 2 | Biannual | bar: June; Dec
| Off-site Pumping Station No. 1 (Unit Lift and Force Ejector Lift wet well cover, pump down and clean sump by jet washing. Replace cover. | 2 | Biannual | bar: June; Dec
| Control Kiosk (P.S. No 1) Carry out thorough clean of the control kiosk, remove cobwebs and dirt. Brush down exterior. | 2 | Biannual | bar: June; Dec
| Off-site Pumping Station No. 2 (Unit Lift and Force Ejector Lift wet well cover, pump down and clean sump by jet washing. Replace cover. | 2 | Biannual | bar: June; Dec
| Control Kiosk (P.S. No. 2) Carry out thorough clean of the control kiosk, remove cobwebs and dirt. Brush down exterior. | 2 | Biannual | bar: June; Dec
| Read and record the electricity and water meters (end of June and December). | 2 | Biannual | bar: June; Dec
| Clean leaves and other accumulated debris from the site and dispose of all arisings to authorised tip. Check overhang of trees and report any encroachment over the treatment units. | 2 | Biannual | bar: June; Dec
| Check soakaway operation (4 No.). Empty accumulated effluent/sludge and clean by jet washing. | 2 | Biannual | bar: June; Dec
| Inspect and clean the re-circulation and sludge pumps as specified. | 2 | Biannual | bar: June; Dec
| Weed kill gravel areas (July) using an approved weed killer suitable for use adjacent to watercourses and above aquifers. | 2 | Biannual | bar: June; Dec
| Check for earth continuity. | 1 | Annual | bar: Dec
| Control Kiosk (P.S. No 1) Check for earth continuity. | 1 | Annual | bar: Dec
| Control Kiosk (P.S. No. 2) Check for earth continuity. | 1 | Annual | bar: Dec

## Manor Road
| STP HAMPSHIRE - Maintenance Item Description, Manor Road | Quantity | Frequency | Apr | May | June | Jul | Aug | Sept | Oct | Nov | Dec | Jan | Feb | Mar
Item | Maintenance works including: | To be reviewed post major planned replacement works installation
Unlock, enter and set telemetry “Engineer on Site” switch. Check security of gates and fences. Check for rodent infestation. Check warning signs, condition of manhole/access covers and frames, ladders, step irons, handrailing, steps and working platforms.
Lift access covers, clean inlet chamber, including interceptor by jet washing. Clean high level alarm float of rags and other debris. Replace covers.
Tidy site.
Clereflo Treatment Plant
Check operation of the re-circulation pumps (3 No.) as specified.
Check and confirm that there are no leaks from exposed pipework.
Check final effluent discharge as specified.
Control Kiosk (All equipment must be isolated before any maintenance work is carried out)
Inspect cables and fittings. Check heater and thermostat setting. Check operation of indicators, lamps, lights and security of earthing straps.
Check/re-set overloads.
Final Effluent Pumping Station
Check operation of pumps (2 No.)
Forward feed air lift pumps
Empty well, clean and inspect pumps
(Before carrying out the following maintenance task ensure that the power is off and the mains isolator is padlocked)
Check for correct operation of the sludge return pump as specified.
Remove access covers and pump down sump and clean by jet washing. Replace covers.
Inspect and clean sample chamber by jet washing.
Clean all manholes and collection pits within the site by jet washing including channels, walls, benching and frame rebates. Clean covers, clear lifting eyes and re-fit.
Clean, check operation and oil all padlocks on site.
Carry out thorough clean of the control kiosk, remove cobwebs, dirt and wipe down exterior.
Read and record the electricity meter (end of June and December).
Clean leaves and other accumulated debris from the site and dispose of all arisings to authorised tip. Check overhang of trees and report any encroachment over the treatment units.
Check condition of outfall (remote from site). Clear away any accumulated debris and cut back overgrowth
Inspect and clean the re-circulation and sludge pumps as specified.
Final Effluent Pumping Station Check condition of pumps as specified.
Weed kill gravel areas using an approved weed killer suitable for use adjacent to watercourses and above aquifers.
Forward feed air lift pumps Check for earth continuity.
Control Kiosk (All equipment must be isolated before any maintenance work is carried out) Check for earth continuity.

## Dean Road
| STP HAMPSHIRE - Maintenance Item Description, Dean Road | Quantity | Frequency | Apr | May | June | Jul | Aug | Sept | Oct | Nov | Dec | Jan | Feb | Mar
Item | Maintenance works including: | To be reviewed post major planned replacement works installation
Unlock, enter and set telemetry “Engineer on Site” switch. Check security of gates and fences. Check for rodent infestation. Check warning signs, condition of manhole/access covers and frames, ladders, step irons, handrailing, steps and working platforms.
Lift access covers and clean channels, weirs, scum boards and dip pipes of inlet chamber and primary balancing tank by jet washing. Clean high level alarm float of rags and other debris. Replace covers
Check/clean flow splitterbox.
Tidy site.
Primary Effluent Pumping Station
Check operation of pumps (2 No.)
Clereflo Treatment Plant
Check operation of the re-circulation pump as specified.
Check and confirm that there are no leaks from exposed pipework.
Check final effluent discharge as specified.
Control Kiosk (All equipment must be isolated before any maintenance work is carried out)
Inspect cables and fittings. Check heater and thermostat setting. Check operation of indicators, lamps, lights and security of earthing straps.
Check/re-set overloads.
Remove access covers and pump down sump and clean by jet washing. Replace covers.
Inspect and clean sample chamber by jet washing.
Clean, check operation and oil all padlocks on site.
Clean all manholes and collection pits within the site by jet washing including channels, wells, benching and frame rebates. Clean covers and clear lifting eyes and re-fit.
Carry out thorough clean of the control kiosk, remove cobwebs, dirt and wipe down exterior.
Read and record the electricity meter quarterly (end of June and December).
Clean leaves and other accumulated debris from the site and dispose of all arisings to authorised tip. Check overhang of trees and report any encroachment over the treatment units.
Check condition of outfall. Clear away any accumulated debris and cut back overgrowth.
Check condition of pumps as specified.
(Before carrying out the following maintenance task ensure that the power is off and the mains isolator is padlocked)
Inspect and clean the re-circulation pump as specified.
Weed kill gravel areas using an approved weed killer suitable for use adjacent to watercourses and above aquifers.
Check for earth continuity.

## East Dean Road
| STP HAMPSHIRE - Maintenance Item Description, East Dean Road | Quantity | Frequency | Apr | May | June | Jul | Aug | Sept | Oct | Nov | Dec | Jan | Feb | Mar
Item | Maintenance works including:
| Unlock, enter and set telemetry “Engineer on Site” switch. Check security of gates and fences. Check for rodent infestation. Check warning signs, condition of manhole/access covers and frames, ladders, step irons, handrailing, steps and working platforms. | 12 | Monthly | bar: Apr to Mar
| Lift access covers and clean channels, weirs, scum boards and dip pipes of inlet chamber and primary balancing tank by jet washing. Clean high level alarm float of rags and other debris. Replace covers. | 12 | Monthly | bar: Apr to Mar
| Tidy site. | 12 | Monthly | bar: Apr to Mar
| Clereflo Treatment Plant | 12 | Monthly | bar: Apr to Mar
| Check operation of the re-circulation pump as specified. | 12 | Monthly | bar: Apr to Mar
| Check and confirm that there are no leaks from exposed pipework. | 12 | Monthly | bar: Apr to Mar
| Check final effluent discharge as specified. | 12 | Monthly | bar: Apr to Mar
Control Kiosk (All equipment must be isolated before any maintenance work is carried out)
| Inspect cables and fittings. Check heater and thermostat setting. Check operation of indicators, lamps, lights and security of earthing straps. | 12 | Monthly | bar: Apr to Mar
| Check/re-set overloads. | 12 | Monthly | bar: Apr to Mar
Forward feed air lift pumps
| Empty well, clean and inspect pumps | 12 | Monthly | bar: Apr to Mar
| Inspect and clean sample/flow meter chamber by jet washing. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Clean, check operation and oil all padlocks on site. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Clean all manholes and collection pits within the site by jet washing including channels, walls, benchings and frame rebates. Clean covers and clear lifting eyes and re-fit. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Carry out thorough clean of the control kiosk, remove cobwebs, dirt and wipe down exterior. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Read and record the electricity meter (end of June and December). | 2 | Biannual | bar: June; Dec
| Clean leaves and other accumulated debris from the site and dispose of all arisings to authorised tip. | 2 | Biannual | bar: June; Dec
| Check condition of headwall at outfall. Clear away any accumulated debris and cut back overgrowth. | 2 | Biannual | bar: June; Dec
(Before carrying out the following maintenance task ensure that the power is off and the mains isolator is padlocked)
| Inspect and clean the re-circulation pump as specified. | 2 | Biannual | bar: June; Dec
| Secondary treatment unit servicing | 2 | Biannual | bar: June; Dec
| Weed kill gravel areas using an approved weed killer suitable for use adjacent to watercourses and above aquifers. | 2 | Biannual | bar: June; Dec
| Check for earth continuity. | 1 | Annual | bar: Dec

## Carter Clays
| STP HAMPSHIRE - Maintenance Item Description, Carters Clay | Quantity | Frequency | Apr | May | June | Jul | Aug | Sept | Oct | Nov | Dec | Jan | Feb | Mar
Item | Maintenance works including:
| Unlock and set “Engineer on Site” switch. Check security of gates and fences. Check for rodent infestation. Check warning signs, condition of manhole covers and frames, ladders, step irons, handrailing and working platforms. | 12 | Monthly | bar: Apr to Mar
| Inspect and clean distributor arms and sparge holes to ensure filter arms are free of debris and effluent is being evenly distributed. Check for surface ponding and report. Clear weeds, leaves and debris from media bed. Clean filter arm rotation sensor. | 12 | Monthly | bar: Apr to Mar
| Lift access covers and clean channels, weirs, scum boards and dip pipes of inlet chamber, settlement tank and humus tank by jet washing. Clean high level alarm float. Replace covers. | 12 | Monthly | bar: Apr to Mar
| Check/clear inlet from ditch into outfall pipe. | 12 | Monthly | bar: Apr to Mar
| Tidy site. | 12 | Monthly | bar: Apr to Mar
| Visual check on effluent. | 12 | Monthly | bar: Apr to Mar
| Check operation of pumps (2No.) | 12 | Monthly | bar: Apr to Mar
| Control Kiosk (All equipment must be isolated before any maintenance work is carried out). | 12 | Monthly | bar: Apr to Mar
| Inspect cables and fittings. Check heater and thermostat setting. Check operation of indicators, lamps, lights and security of earthing straps. | 12 | Monthly | bar: Apr to Mar
| Check/re-set overloads. | 12 | Monthly | bar: Apr to Mar
| Remove access covers and pump down sump and clean by jet washing. Replace covers. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Ensure filter air vents are clear of obstructions. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Inspect and clean sample chamber by jet washing. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Clean all manholes and collection pits within the site by jet washing including channels, walls, benchings and frame rebates. Clean covers and clean lifting eyes of debris and refit. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Check filter arms for ‘soundness’. Check and rectify any faults with connections to the main distributor body, tension cables and adjusters. Grease/oil moving parts in accordance with Manufacturer’s recommendations. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Clean and check operation and oil padlocks on site. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| (Check operation of break tank valve, ball valve and drain down. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Carry out thorough clean of the control kiosk, remove cobwebs and dirt. Brush down exterior. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Check condition of pumps as specified. | 2 | Biannual | bar: June; Dec
| Read and record the electricity and water meters (end of June and December) | 2 | Biannual | bar: June; Dec
| Clean leaves and other accumulated debris from the site and dispose of all arisings to authorised tip. Check overhang of trees and report any encroachment over the treatment units. | 2 | Biannual | bar: June; Dec
| Check/clear outfall pipe by jet washing. Clear away any accumulated debris and overgrowth at headwall into ditch. | 2 | Biannual | bar: June; Dec
| Weedkill gravel areas using an approved weed killer suitable for use adjacent to watercourses and above aquifers. | 2 | Biannual | bar: June; Dec
| Cut back hedge growth. | 1 | Annual | bar: Dec
| Check for earth continuity. | 4 | Qtr. | bar: June; Sept; Dec; Mar

## Lymer Villas
| STP HAMPSHIRE - Maintenance Item Description, Lymer Villas | Quantity | Frequency | Apr | May | June | Jul | Aug | Sept | Oct | Nov | Dec | Jan | Feb | Mar
Item | Maintenance works including:
| Unlock, check security of gates and fences. Check for rodent infestation. Check warning signs, condition of manhole covers and frames, ladders, step irons, handrailing and working platforms. | 12 | Monthly | bar: Apr to Mar
| Lift access covers, inspect and clean distributor arms to ensure filter arms are free of debris and effluent is being evenly distributed. Check for surface ponding and report. Replace covers | 12 | Monthly | bar: Apr to Mar
| Lift access covers and clean channels, weirs, scum boards and dip pipes of inlet chamber, settlement tank and humus tank by jet washing. Replace covers | 12 | Monthly | bar: Apr to Mar
| Tidy site. | 12 | Monthly | bar: Apr to Mar
| Visual check on effluent. | 12 | Monthly | bar: Apr to Mar
2.5 HT1 Humus Tank
(All equipment must be isolated before any maintenance work on any electrical items of plant is carried out)
| Check quality of final effluent. If cloudy or contains suspended particles rectify as specified. | 12 | Monthly | bar: Apr to Mar
Filter Effluent Pumping Station
| Check operation of pumps (2No) | 12 | Monthly | bar: Apr to Mar
Control Kiosk (All equipment must be isolated before any maintenance work is carried out).
| Inspect cables and fittings. Check heater and thermostat setting. Check operation of indicators, lamps, lights and security of earthing straps. | 12 | Monthly | bar: Apr to Mar
| Check/re-set overloads. | 12 | Monthly | bar: Apr to Mar
| Check filter arms for ‘soundness’. Check and rectify any faults with connections to the main distributor body, tension rods and adjusters. Grease/oil moving parts in accordance with Manufacturer’s recommendations. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Check for correct operation of the sludge return pump as specified. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Remove access covers and pump down sump and clean by jet washing. Replace covers | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Check operation of break tank valve, ball valve and drain down. Read and record the water meter. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Ensure filter vents are clear of obstructions. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Clean all manholes and collection pits within the site by jet washing including channels; walls, benchings and frame rebates. Clean covers and clean lifting eyes of debris and refit. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Clean and check operation and oil padlocks on site. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Check filter distribution system generally for wear and tear and report on findings. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Check filter distribution system is level and adjust if necessary in accordance with O & M Manual. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Carry out thorough clean of the control kiosk, remove cobwebs and dirt. Brush down exterior | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Remove, inspect, clean and re-position sludge return pump as specified. | 2 | Biannual | bar: June; Dec
| Check condition of pumps as specified | 2 | Biannual | bar: June; Dec
| Read and record electricity meter reading (end of June and December) | 2 | Biannual | bar: June; Dec
| After leaf fall in autumn collect all leaves and dispose to authorised tip. Check overhang of trees and report any encroachment over the treatment units. | 1 | Annual | bar: Dec
| Weed kill gravelled areas using an approved weed killer suitable for use adjacent to water-courses and above aquifers. | 2 | Biannual | bar: June; Dec
| Check for earth continuity. | 1 | Annual | bar: Dec

## Green Pond Lane
| STP HAMPSHIRE - Maintenance Item Description, Green Pond Lane | Quantity | Frequency | Apr | May | June | Jul | Aug | Sept | Oct | Nov | Dec | Jan | Feb | Mar
Item | Maintenance works including:
1 | Unlock and set “Engineer on Site” switch. Check security of gates and fences. Check for rodent infestation. Check warning signs, condition of manhole covers and frames, ladders, step irons, handrailing and working platforms. | 12 | Monthly | bar: Apr to Mar
2 | Inspect and clean distributor arms and sparge holes to ensure filter arms are free of debris and effluent is being evenly distributed. Check for surface ponding and report. Clear weeds, leaves and debris from media bed. | 12 | Monthly | bar: Apr to Mar
3 | (iii)Lift access covers and clean channels, weirs, scum boards and dip pipes of inlet chamber, settlement tanks (2 No.) and humus tank by jet washing. Replace covers. | 12 | Monthly | bar: Apr to Mar
4 | Tidy site. | 12 | Monthly | bar: Apr to Mar
5 | Visual check on effluent. | 12 | Monthly | bar: Apr to Mar
11 | Clean and check operation and oil padlocks on site. | 12 | Monthly | bar: Apr to Mar
6 | Generator inspect and check levels, record hours run. Service as per manufacturers handbook | 12 | Monthly | bar: Apr to Mar
7 | check deisel oil level order as required | 12 | Monthly | bar: Apr to Mar
8 | Ensure filter air vents are clear of obstructions. | 4 | Qtr. | bar: June; Sept; Dec; Mar
9 | Clean all manholes and collection pits within the site by jet washing including channels, walls, benchings and frame rebates. Clean covers and clean lifting eyes of debris and refit. | 4 | Qtr. | bar: June; Sept; Dec; Mar
10 | Check filter arms for ‘soundness’. Check and rectify any faults with connections to the main distributor body, tension cables and adjusters. Grease/oil moving parts in accordance with Manufacturer’s recommendations. | 4 | Qtr. | bar: June; Sept; Dec; Mar
12 | (v) Cut grass and weeds to keep them short and prevent seeding four times/annum (April, June, August and September) Remove cuttings to authorised tip. Strim around fence lines, tanks, gates and outer perimeter of grassed area. | 4 | Qtr. | bar: June; Sept; Dec; Mar

## Glebe Meadow
| STP HAMPSHIRE - Maintenance Item Description, Glebe Meadow | Quantity | Frequency | Apr | May | June | Jul | Aug | Sept | Oct | Nov | Dec | Jan | Feb | Mar
Item | Maintenance works including:
| Unlock, enter and set telemetry “Engineer on Site” switch, check security of gates and fences, Check for rodent infestation. Check warning signs, condition of manhole covers and frames, ladders, step irons, hand-railing and working platforms. | 12 | Monthly | bar: Apr to Mar
| Check/clean flow splitter box. | 12 | Monthly | bar: Apr to Mar
| Tidy site. | 12 | Monthly | bar: Apr to Mar
| (iLift access covers, inspect and clean distributor arms and sparge holes to ensure filter arms are free of debris and effluent is being evenly distributed. Check for surface ponding and report. Clean filter arm rotation sensor. Replace covers. | 12 | Monthly | bar: Apr to Mar
| Lift access covers and clean channels, weirs, scum boards and dip pipes of inlet chamber, settlement tank and humus tank by jet washing. Clean high level alarm float of rags and other debris. Replace covers. | 12 | Monthly | bar: Apr to Mar
| Clean sample chamber walls and floor by jet washing. | 12 | Monthly | bar: Apr to Mar
| Ensure filter air vents are clear of obstructions and jet wash to clean silt build up from channel tiles. | 12 | Monthly | bar: Apr to Mar
| 2.5 HT1 Humus Tank | 12 | Monthly | bar: Apr to Mar
(All equipment must be isolated before any maintenance work on any electrical items of plant is carried out)
| Check quality of final effluent. If cloudy or contains suspended particles rectify as specified. | 12 | Monthly | bar: Apr to Mar
| Filter Effluent Pumping Station | 12 | Monthly | bar: Apr to Mar
| Check operation of pumps (2No.) | 12 | Monthly | bar: Apr to Mar
| Control Kiosk (All equipment must be isolated before any maintenance work is carried out) | 12 | Monthly | bar: Apr to Mar
| Inspect cables and fittings. Check heater and thermostat setting. Check operation of indicators, lamps, lights and security of earthing straps. | 12 | Monthly | bar: Apr to Mar
| Check/re-set overloads. | 12 | Monthly | bar: Apr to Mar
| Check for correct operation of the sludge return pump as specified. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Remove access covers and pump down sump and clean by jet washing. Replace covers. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Clean all manholes and collection pits within the site by jet washing including channels, walls, benchings and frame rebates. Clean covers and clear lifting eyes of debris and refit. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Check filter arms for ‘soundness’. Check and rectify any faults with connections to the main distributor body, tension cables and adjusters. Grease/oil all moving parts. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Cut grass and weeds along the reinforced grassed access road to prevent seeding four times per annum (April, June, August and September). Remove cuttings to authorised tip. Strim around fence lines and outer perimeter of grassed areas. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Carry out thorough clean of the control kiosk, remove cobwebs, dirt and clean exterior. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Read and record the electricity meter quarterly (end of June & December). | 2 | Biannual | bar: June; Dec
| Jet clean the pipe not exceeding 150mm diameter between humus tank and headwall. Clean headwall structure by jet washing. | 2 | Biannual | bar: June; Dec
| Remove, inspect, clean and re-position sludge return pump as specified. | 2 | Biannual | bar: June; Dec
| Filter Effluent Pumping Station Check condition of pumps as specified. | 2 | Biannual | bar: June; Dec
| Clean, check operation and oil all padlocks on site. | 1 | Annual | bar: Dec
| After leaf fall in autumn collect all leaves and dispose to authorised tip. Check overhang of trees and report any encroachment over the treatment units. | 1 | Annual | bar: Dec
| Weed kill gravelled areas using an approved weed killer suitable for use adjacent to water-courses and above aquifers. | 2 | Biannual | bar: June; Dec
| Check for earth continuity. | 1 | Annual | bar: Dec

## The Close
| STP HAMPSHIRE - Maintenance Item Description, The Close | Quantity | Frequency | Apr | May | June | Jul | Aug | Sept | Oct | Nov | Dec | Jan | Feb | Mar
Item | Maintenance works including:
| Unlock, enter and set telemetry “Engineer on Site” switch. Check security of gates and fences. Check for rodent infestation. Check warning signs, condition of manhole/access covers and frames, ladders, step irons, hand railing, steps and working platforms. | 12 | Monthly | bar: Apr to Mar
| Isolate electricity supply and remove covers from Biodisc unit and check appearance of biomass packs as specified. Visually check the general condition of the plant ensuring that pack retaining fixings are secure. Replace covers and reinstate power supply. | 12 | Monthly | bar: Apr to Mar
| (iii) Lift access covers and clean high level alarm float and loss of rotation sensor. | 12 | Monthly | bar: Apr to Mar
| (iv) Tidy site. | 12 | Monthly | bar: Apr to Mar
| (v) Visual check on effluent. | 12 | Monthly | bar: Apr to Mar
Control Kiosk (All equipment must be isolated before any maintenance work is carried out)
| Check cabling, plug-in devices and other fittings and switches. Check heater and thermostat setting. Check operation of instruments, indicators, lamps and security of earthing straps all as specified. | 12 | Monthly | bar: Apr to Mar
| (i) Check operation of break tank valve, ball valve and drain down. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| (ii) Inspect and clean sample/flow meter chamber by jet washing. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| (iii) Clean, check operation and oil all padlocks. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Cut the grass and weeds to keep them short and prevent seeding four times per annum (April, June, August and September). Remove cuttings to authorised tip. Strim around fence lines, gates and structures. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Carry out thorough clean of the control kiosk, remove cobwebs and dirt and brush down exterior. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Read and record the electricity and water meters (end of June and December). | 2 | Biannual | bar: June; Dec
Klargester Biodisc Plant
| Carry out service of Biodisc unit as per Klargester Environmental Engineering’s inspection schedule. | 2 | Biannual | bar: June; Dec
| Check security of fuses, contractors, relays, timers, display instruments and indicator lamps. Check for overheating, burning and freedom of operation all as specified. | 2 | Biannual | bar: June; Dec
| (i) Check soakaway operation. Empty any accumulated effluent/sludge and clean by jet washing. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| After leaf fall in autumn collect all leaves and dispose to authorised tip. Check overhang of trees and report any encroachment over the plant and ancillary structures. | 2 | Biannual | bar: June; Dec
| Weed kill paved areas using an approved weed killer suitable for use adjacent to water courses and above aquifers. | 2 | Biannual | bar: June; Dec
| Check all bolted main cable joints for security/overheating. Remove deposits of dust or dirt from inside the control cabinet. | 2 | Biannual | bar: June; Dec

## Cowleas Cottages
| STP Hampshire - Maintenance Item Description, Cowleas Cottages | Quantity | Frequency | Apr | May | June | Jul | Aug | Sept | Oct | Nov | Dec | Jan | Feb | Mar
Item | Maintenance works including:
| Unlock, enter and set telemetry “Engineer on Site” switch, check security of gates and fences, Check for rodent infestation. Check warning signs, condition of manhole covers and frames, ladders, step irons, hand-railing and working platforms. | 12 | Monthly | bar: Apr to Mar
| Lift access covers, inspect and clean distributor arms and sparge holes to ensure filter arms are free of debris and effluent is being evenly distributed. Check for surface ponding and report. Clean filter arm rotation sensor. Replace covers (2 No. filters). | 12 | Monthly | bar: Apr to Mar
| Remove Copasacs and dispose to authorised tip. Clean frame and fit new bags. (2 No.). | 12 | Monthly | bar: Apr to Mar
| Lift access covers and clean channels, weirs, scum boards and dip pipes of inlet chamber, settlement tanks (2 No.) and humus tanks (2 No.) by jet washing. Clean high level alarm float of rags and debris. Replace covers. | 12 | Monthly | bar: Apr to Mar
| Clean sample/flow meter chamber walls, floor and v-notch and baffle by jet washing. Remove debris from behind v-notch weir. Wipe clean lenses of flow meter/temperature sensors. | 12 | Monthly | bar: Apr to Mar
| Visual check on effluent. | 12 | Monthly | bar: Apr to Mar
| Control Kiosk (All equipment must be isolated before any maintenance work is carried out). | 12 | Monthly | bar: Apr to Mar
| Inspect cables and fittings. Check heater and thermostat setting. Check operation of indicators, lamps, lights and security of earthing straps. | 12 | Monthly | bar: Apr to Mar
| Check/re-set overloads. | 12 | Monthly | bar: Apr to Mar
| Control Kiosk (Pumping Station) | 12 | Monthly | bar: Apr to Mar
| (All equipment must be isolated before any maintenance work is carried out) | 12 | Monthly | bar: Apr to Mar
| Inspect cables and fittings. Check heater and thermostat setting. Check operation of indicators, lamps, lights and security of earthing straps | 12 | Monthly | bar: Apr to Mar
| Check/re-set overloads. | 12 | Monthly | bar: Apr to Mar
| Tidy site. | 12 | Monthly | bar: Apr to Mar
Off-Site Pumping Station
(Unit Lift and Force Ejector)
LOCATED AT COWLEAS CLOSE
| Lift wet well cover, lift and clean floats of rags and other debris. Replace cover. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Check and clean pump by manual operation. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Check compressor oil levels and condition and top up as required. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| (i) Ensure filter air vents are clear of obstructions and jet wash to clean silt build up from channel tiles. (2 No. filers). | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Clean all manholes and collection pits within the site by jet washing including channels, walls, benchings and frame rebates. Clean covers and clear lifting eyes of debris and refit. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Cut the grass and weeds to keep them short and prevent seeding four times per annum (April, June, August and September). Remove cuttings to authorised tip. Strim around fence lines, tanks, gates and outer perimeter of grassed areas. (Approx. 300 m2) | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Carry out thorough clean of the control kiosk, remove cobwebs, dirt and wipe down exterior. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Off-Site Pumping Station Lift wet well cover, pump down and clean sump by jet washing. Replace cover. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Carry out thorough clean of the control kiosk, remove cobwebs, dirt and brush down exterior. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Read and record the electricity and water meters (end of June & December). | 2 | Biannual | bar: June; Dec
| Clean, check operational and oil all padlocks on site. | 2 | Biannual | bar: June; Dec
| Jet clean the pipe not exceeding 150mm diameter between humus tanks and headwall. Clean headwall structure by jet washing. Cut back any overgrowth. | 2 | Biannual | bar: June; Dec
| Carry out checks on valves, gauges, pressure readings, drive belts, air pipework, vacuum chamber etc as per inspection schedule (Tuke & Bell Ltd) | 2 | Biannual | bar: June; Dec
| Control Kiosk (All equipment must be isolated before any maintenance work is carried out). Check for earth continuity. | 1 | Annual | bar: Dec
| Control Kiosk (Pumping Station) Check for earth continuity. | 1 | Annual | bar: Dec

## Butlers Close
| STP Hampshire - Maintenance Item Description, Butlers Close | Quantity | Frequency | Apr | May | June | Jul | Aug | Sept | Oct | Nov | Dec | Jan | Feb | Mar
Item | Maintenance works including:
| Unlock, enter and set telemetry “Engineer on Site” switch. Check security of gates and fences. Check for rodent infestation. Check warning signs, condition of manhole/access covers and frames, ladders, step irons, hand railing, steps and working platforms. | 12 | Monthly | bar: Apr to Mar
| Tidy site. | 12 | Monthly | bar: Apr to Mar
| Visual check on effluent. | 12 | Monthly | bar: Apr to Mar
Aeration Plant (Works B)
| Inspect and check aeration plant to ensure it is functioning correctly all as specified. . | 12 | Monthly | bar: Apr to Mar
| Check/adjust operation of blowers, lubrication, maintenance of air cleaners, belt tension all as specified. | 12 | Monthly | bar: Apr to Mar
| Control Panel (All equipment must be isolated before any maintenance work is carried out) | 12 | Monthly | bar: Apr to Mar
| Check cabling, plug-in devices and other fittings and switches. Check heater and thermostat setting. Check operation of instruments, indicators, lamps and security of earthing straps all as specified. | 12 | Monthly | bar: Apr to Mar
Agisac Fine Screening System
(All equipment must be isolated before any maintenance work is carried out)
| Wash unit with mains water/domestic detergent mixture as specified. | 12 | Monthly | bar: Apr to Mar
| Check tightness of all nuts and bolts as specified | 12 | Monthly | bar: Apr to Mar
| Grease all bearings as specified. | 12 | Monthly | bar: Apr to Mar
| Aeration Plant (Works B) Check air distribution and adjust if necessary | 12 | Monthly | bar: Apr to Mar
| Check security of fuses, contactors, relays, timers, display instruments and indictor lamps. Check for overheating, burning and freedom of operation all as specified. | 12 | Monthly | bar: Apr to Mar
| Agisac Fine Screening System Check for excessive play in the agitation mechanism bearings and linkages as specified. | 12 | Monthly | bar: Apr to Mar
| (i) Clean, check operation and oil all padlocks on site. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Inspect headwall at outfall for condition and operation. (Headwall is remote from site) | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Cut the grass and weeds to keep them short and prevent seeding four times per annum (April, June, August and September). Remove cuttings to authorised tip. Strim around fence lines tanks, gates and outer perimeter of ground areas | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Ensure filter air vents are clear of obstructions and jet wash to clean silt build up from channel tiles. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Clean all manholes and collection pits within the site by jet washing including channels, walls, benchings and frame rebates. Clean covers and clear lifting eyes of debris and refit. | 4 | Qtr. | bar: June; Sept; Dec; Mar
Control Building (All equipment must be isolated before any maintenance work is carried out)
| Clear building of any accumulated debris, cobwebs, dirt and brush down exterior. | 4 | Qtr. | bar: June; Sept; Dec; Mar
Effluent Pumping Station
| Carry out routine service as specified. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Read and record the electricity and water meters (end of June & December) | 2 | Biannual | bar: June; Dec
| Check plant for build up of scum and grease. Clean as specified if necessary. | 2 | Biannual | bar: June; Dec
| Control Panel (All equipment must be isolated before any maintenance work is carried out) Check all bolted main cable joints for security/overheating. Remove deposits of dust from inside the control cabinet. | 2 | Biannual | bar: June; Dec
| After leaf fall in autumn, collect all leaves and dispose to authorised tip. Check overhang of trees and report any encroachment over the treatment plant. | 1 | Annual | bar: Dec
| Weed kill gravel areas and vehicle access using an approved weed killer suitable for use adjacent to water-courses and above aquifers. | 2 | Biannual | bar: June; Dec
| Agisac Fine Screening System Check Agisacs and change when one-third full or contain approx. 8 kgs of collected debris. Dispose of used Agisacs to authorised tip. Clean frame and fit new bags. | 2 | Biannual | bar: June; Dec
| Raise pumps inspect for noise and vibration. Check oil and replace if contaminated. Check for impeller wear or damage and confirm correct rotation. | 4 | Qtr. | bar: June; Sept; Dec; Mar

## Oval Road
| STP Hampshire - Maintenance Item Description, Oval Road | Quantity | Frequency | Apr | May | June | Jul | Aug | Sept | Oct | Nov | Dec | Jan | Feb | Mar
Item | Maintenance works including:
| Unlock, enter and set telemetry “Engineer on Site” switch. Check security of gates and fences. Check for rodent infestation. Check warning signs, condition of manhole/access covers and frames, ladders, step irons, hand railing, steps and working platforms. | 12 | Monthly | bar: Apr to Mar
| Tidy site. | 12 | Monthly | bar: Apr to Mar
| Visual check on effluent. | 12 | Monthly | bar: Apr to Mar
Biological Treatment Plant (Works A)
| Lift access covers, inspect and clean distributor arms and sparge holes to ensure that effluent is being evenly distributed. Check for surface ponding and report. Replace covers. Clean filter arm rotation sensor. | 12 | Monthly | bar: Apr to Mar
| Remove Copasac and dispose to authorised tip. Clean frame and fit new bag. | 12 | Monthly | bar: Apr to Mar
| Lift access covers and clean channels, weirs and scum boards of settlement tank and humus tank by jet washing. Clean high level alarm float of rags and other debris. Replace covers. | 12 | Monthly | bar: Apr to Mar
| Clean sample/flow meter chamber walls, floor and v-notch and baffle by jet washing. Remove debris from behind v-notch weir. Wipe clean lenses of flow meter/temperature sensors. | 12 | Monthly | bar: Apr to Mar
| (i) Clean, check operation and oil all padlocks on site. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Cut the grass and weeds to keep them short and prevent seeding four times per annum (April, June, August and September). Remove cuttings to authorised tip. Strim around fence lines tanks, gates and outer perimeter of ground areas | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Ensure filter air vents are clear of obstructions and jet wash to clean silt build up from channel tiles. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Clean all manholes and collection pits within the site by jet washing including channels, walls, benchings and frame rebates. Clean covers and clear lifting eyes of debris and refit. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Check operation of break tank valve, ball valve and drain down. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Check filter arms for ‘soundness’. Check and rectify any faults with connections to the main distributor body, tension cables and adjusters. Grease/oil moving parts. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Read and record the electricity and water meters (end of June & December) | 2 | Biannual | bar: June; Dec
| Check plant for build up of scum and grease. Clean as specified if necessary. | 2 | Biannual | bar: June; Dec
| Control Panel (All equipment must be isolated before any maintenance work is carried out) Check all bolted main cable joints for security/overheating. Remove deposits of dust from inside the control cabinet. | 2 | Biannual | bar: June; Dec
| After leaf fall in autumn, collect all leaves and dispose to authorised tip. Check overhang of trees and report any encroachment over the treatment plant. | 1 | Annual | bar: Dec
| Weed kill gravel areas and vehicle access using an approved weed killer suitable for use adjacent to water-courses and above aquifers. | 2 | Biannual | bar: June; Dec
| Agisac Fine Screening System Check Agisacs and change when one-third full or contain approx. 8 kgs of collected debris. Dispose of used Agisacs to authorised tip. Clean frame and fit new bags. | 2 | Biannual | bar: June; Dec

## Pragnells Cottages
| STP HAMPSHIRE - Maintenance Item Description, Pragnells Cottages | Quantity | Frequency | Apr | May | June | Jul | Aug | Sept | Oct | Nov | Dec | Jan | Feb | Mar
Item | Maintenance works including:
| Unlock, enter and set telemetry “Engineer on Site” switch. Check security of gates and fences. Check for rodent infestation. Check warning signs, condition of manhole covers and frames, ladders, step irons, handrailing and working platforms. | 12 | Monthly | bar: Apr to Mar
| Lift access covers and clean high level alarm float of rags and other debris, Replace covers. | 12 | Monthly | bar: Apr to Mar
| Tidy site. | 12 | Monthly | bar: Apr to Mar
* Note site is not fenced with treatment plant, control cabinet and irrigation area in different locations as shown on locations plan.
(Before carrying out the following maintenance task ensure that the power is off and the mains isolator is padlocked)
| Check operation of the re-circulation pump as specified. | 12 | Monthly | bar: Apr to Mar
| Check operation of effluent pump as specified. | 12 | Monthly | bar: Apr to Mar
| (iii) Check and confirm that there are no leaks from exposed pipework. | 12 | Monthly | bar: Apr to Mar
| (iv) Check final effluent discharge as specified. | 12 | Monthly | bar: Apr to Mar
Control Kiosk (All equipment must be isolated before any maintenance work is carried out)
| Inspect cables and fittings. Check heater and thermostat setting. Check operation of indicators, lamps, lights, and security of earthing straps. | 12 | Monthly | bar: Apr to Mar
| check/re-set overloads. | 12 | Monthly | bar: Apr to Mar
| Inspect and clean sample chamber by jet washing. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Clean all manholes and collection pits within the site by jet washing including channels; walls, benchings and frame rebates. Clean covers and clean lifting eyes of debris and refit. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Clean, check operation and oil padlocks on site. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Carry out thorough clean of the control kiosk, remove cobwebs, dirt and wipe down exterior. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Read and record the electricity meter (end of June and December). | 2 | Biannual | bar: June; Dec
| Check for earth continuity. | 1 | Annual | bar: Dec

## Hill Place
| TP HAMPSHIRE - Maintenance Item Description, Hill Place | Quantity | Frequency | Apr | May | June | Jul | Aug | Sept | Oct | Nov | Dec | Jan | Feb | Mar
Item | Maintenance works including:
| unlock, enter and set telemetry “Engineer on Site” switch. Check security of gates and fences. Check for rodent infestation. Check warning signs, condition of manhole/access covers and frames, ladders, step irons, hand railing, steps and working platforms. | 12 | Monthly | bar: Apr to Mar
Condor Clerflo plant type E Aeriation unit
| Tidy site. | 12 | Monthly | bar: Apr to Mar
| Visual check on effluent. | 12 | Monthly | bar: Apr to Mar
| Inspect and clean sample/flow meter chamber by jet washing. | 12 | Monthly | bar: Apr to Mar
| Clean, check operation and oil all padlocks. | 4 | Qtr. | bar: June; Sept; Dec; Mar
Control Kiosk (All equipment must be isolated before any maintenance work is carried out)
| Check cabling, plug-in devices and other fittings and switches. Check heater and thermostat setting. Check operation of instruments, indicators, lamps and security of earthing straps all as specified. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Carry out thorough clean of the control kiosk, remove cobwebs and dirt and brush down exterior. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| After leaf fall in autumn collect all leaves and dispose to authorised tip. Check overhang of trees and report any encroachment over the plant and ancillary structures. | 2 | Biannual | bar: June; Dec
| Weed kill paved areas using an approved weed killer suitable for use adjacent to water courses and above aquifers. | 2 | Biannual | bar: June; Dec
| Carry out service of Clerflo unit as per Condor's inspection schedule. | 2 | Biannual | bar: June; Dec
| Check security of fuses, contractors, relays, timers, display instruments and indicator lamps. Check for overheating, burning and freedom of operation all as specified. | 2 | Biannual | bar: June; Dec
| Cut the grass and weeds to keep them short and prevent seeding four times per annum (April, June, August and September). Remove cuttings to authorised tip. Strim around fence lines, gates and structures. | 1 | Annual | bar: Dec
| Read and record the electricity meter | 2 | Biannual | bar: June; Dec
| Check soakaway operation. Empty any accumulated effluent/sludge and clean by jet washing. | 1 | Annual | bar: Dec
| Check all bolted main cable joints for security/overheating. Remove deposits of dust or dirt from inside the control cabinet. | 1 | Annual | bar: Dec

## Kennet Valley Mews
| TP HAMPSHIRE - Maintenance Item Description, Kennet Valley Mews | Quantity | Frequency | Apr | May | June | Jul | Aug | Sept | Oct | Nov | Dec | Jan | Feb | Mar
Condor Clerflo plant type E Aeriation unit
Item | Maintenance works including:
| Unlock, enter and set telemetry “Engineer on Site” switch. Check security of gates and fences. Check for rodent infestation. Check warning signs, condition of manhole/access covers and frames, ladders, step irons, hand railing, steps and working platforms. | 12 | Monthly | bar: Apr to Mar
| Lift access covers and clean high level alarm float and loss of rotation sensor. | 12 | Monthly | bar: Apr to Mar
| Tidy site. | 12 | Monthly | bar: Apr to Mar
| Visual check on effluent. | 12 | Monthly | bar: Apr to Mar
| Inspect and clean sample/flow meter chamber by jet washing. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Clean, check operation and oil all padlocks. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Cut the grass and weeds to keep them short and prevent seeding four times per annum (April, June, August and September). Remove cuttings to authorised tip. Strim around fence lines, gates and structures. | 4 | Qtr. | bar: June; Sept; Dec; Mar
Control Kiosk (All equipment must be isolated before any maintenance work is carried out)
| Check cabling, plug-in devices and other fittings and switches. Check heater and thermostat setting. Check operation of instruments, indicators, lamps and security of earthing straps all as specified. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Read and record the electricity and water meters (end of June and December). | 2 | Biannual | bar: June; Dec
| After leaf fall in autumn collect all leaves and dispose to authorised tip. Check overhang of trees and report any encroachment over the plant and ancillary structures. | 2 | Biannual | bar: June; Dec
| Weed kill paved areas using an approved weed killer suitable for use adjacent to water courses and above aquifers. | 2 | Biannual | bar: June; Dec
| Carry out service of Clerflo unit as per Condor's inspection schedule. | 2 | Biannual | bar: June; Dec
| Carry out thorough clean of the control kiosk, remove cobwebs and dirt and brush down exterior. | 2 | Biannual | bar: June; Dec
| Check soakaway operation. Empty any accumulated effluent/sludge and clean by jet washing. | 1 | Annual | bar: Dec
| Check security of fuses, contractors, relays, timers, display instruments and indicator lamps. Check for overheating, burning and freedom of operation all as specified. | 1 | Annual | bar: Dec
| Check all bolted main cable joints for security/overheating. Remove deposits of dust or dirt from inside the control cabinet. | 1 | Annual | bar: Dec

## Church View
| STP Somerset - Maintenance Item Description, Church View | Quantity | Frequency | Apr | May | June | Jul | Aug | Sept | Oct | Nov | Dec | Jan | Feb | Mar
Item | Maintenance works including:
| Unlock, enter and set telemetry “Engineer on Site” switch. Check security of gates and fences. Check for rodent infestation. Check warning signs, condition of manhole/access covers and frames, ladders, step irons, hand railing, steps and working platforms. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Isolate electricity supply and remove covers from Biodisc unit and check appearance of biomass packs as specified. Visually check the general condition of the plant ensuring that pack retaining fixings are secure. Replace covers and reinstate power supply. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Lift access covers and clean high level alarm float and loss of rotation sensor. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Tidy site. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Visual check on effluent. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Inspect and clean sample/flow meter chamber by jet washing. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Clean, check operation and oil all padlocks. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Cut the grass and weeds to keep them short and prevent seeding four times per annum (April, June, August and September). Remove cuttings to authorised tip. Strim around fence lines, gates and structures. | 4 | Qtr. | bar: June; Sept; Dec; Mar
Control Kiosk (All equipment must be isolated before any maintenance work is carried out)
| Check cabling, plug-in devices and other fittings and switches. Check heater and thermostat setting. Check operation of instruments, indicators, lamps and security of earthing straps all as specified. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Read and record the electricity and water meters (end of June and December). | 2 | Biannual | bar: June; Dec
| (iii) Weed kill paved areas using an approved weed killer suitable for use adjacent to water courses and above aquifers. | 2 | Biannual | bar: June; Dec
Klargester Biodisc Plant
| Carry out service of Biodisc unit as per Klargester Environmental Engineering’s inspection schedule. | 2 | Biannual | bar: June; Dec
| After leaf fall in autumn collect all leaves and dispose to authorised tip. Check overhang of trees and report any encroachment over the plant and ancillary structures. | 1 | Annual | bar: Dec

## Pilton Road
| STP Somerset - Maintenance Item Description, Pilton Road | Quantity | Frequency | Apr | May | June | Jul | Aug | Sept | Oct | Nov | Dec | Jan | Feb | Mar
Item | Maintenance works including:
| Check security of gates and fences. Check for rodent infestation. Check warning signs, condition of manhole/access covers and frames, ladders, step irons, hand railing, steps and working platforms. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Isolate electricity supply and remove covers from Biodisc unit and check appearance of biomass packs as specified. Visually check the general condition of the plant ensuring that pack retaining fixings are secure. Replace covers and reinstate power supply. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Lift access covers and clean high level alarm float and loss of rotation sensor. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Tidy site. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Visual check on effluent. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Control Kiosk (All equipment must be isolated before any maintenance work is carried out) | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Check cabling, plug-in devices and other fittings and switches. Check heater and thermostat setting. Check operation of instruments, indicators, lamps and security of earthing straps all as specified. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Inspect and clean sample/flow meter chamber by jet washing. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Clean, check operation and oil all padlocks. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Cut the grass and weeds to keep them short and prevent seeding four times per annum (April, June, August and September). Remove cuttings to authorised tip. Strim around fence lines, gates and structures. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Carry out thorough clean of the control kiosk, remove cobwebs and dirt and brush down exterior. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Read and record the electricity and water meters (end of June and December). | 2 | Biannual | bar: June; Dec
Klargester Biodisc Plant
| Carry out service of Biodisc unit as per Klargester Environmental Engineering’s inspection schedule. | 2 | Biannual | bar: June; Dec
| Check security of fuses, contractors, relays, timers, display instruments and indicator lamps. Check for overheating, burning and freedom of operation all as specified. | 2 | Biannual | bar: June; Dec
| After leaf fall in autumn collect all leaves and dispose to authorised tip. Check overhang of trees and report any encroachment over the plant and ancillary structures. | 1 | Annual | bar: Dec
| Weed kill paved areas using an approved weed killer suitable for use adjacent to water courses and above aquifers. | 2 | Biannual | bar: June; Dec

## Fosse Cottages
| STP Somerset - Maintenance Item Description, Fosse Cottages | Quantity | Frequency | Apr | May | June | Jul | Aug | Sept | Oct | Nov | Dec | Jan | Feb | Mar
Item | Maintenance works including:
| Unlock, enter and set telemetry “Engineer on Site” switch. Check security of gates and fences. Check for rodent infestation. Check warning signs, condition of manhole/access covers and frames, ladders, step irons, hand railing, steps and working platforms. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Isolate electricity supply and remove covers from Biodisc unit and check appearance of biomass packs as specified. Visually check the general condition of the plant ensuring that pack retaining fixings are secure. Replace covers and reinstate power supply. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Lift access covers and clean high level alarm float and loss of rotation sensor. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Tidy site. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Visual check on effluent. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Control Kiosk (All equipment must be isolated before any maintenance work is carried out) | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Check cabling, plug-in devices and other fittings and switches. Check heater and thermostat setting. Check operation of instruments, indicators, lamps and security of earthing straps all as specified. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Inspect and clean sample/flow meter chamber by jet washing. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Clean, check operation and oil all padlocks. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Remove weeds to keep short and prevent seeding four times per annum (April, June, August and September). Remove cuttings to authorised tip. Strim around fence lines, gates and structures | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Carry out thorough clean of the control kiosk, remove cobwebs and dirt and brush down exterior. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Read and record the electricity and water meters (end of June and December). | 2 | Biannual | bar: June; Dec
Klargester Biodisc Plant
| Carry out service of Biodisc unit as per Klargester Environmental Engineering’s inspection schedule. | 2 | Biannual | bar: June; Dec
| Check security of fuses, contractors, relays, timers, display instruments and indicator lamps. Check for overheating, burning and freedom of operation all as specified. | 2 | Biannual | bar: June; Dec

## Keward House
| STP Somerset - Maintenance Item Description, Keward House | Quantity | Frequency | Apr | May | June | Jul | Aug | Sept | Oct | Nov | Dec | Jan | Feb | Mar
Item | Maintenance works including:
| Unlock, enter and set telemetry “Engineer on Site” switch. Check security of gates and fences. Check for rodent infestation. Check warning signs, condition of manhole/access covers and frames, ladders, step irons, hand railing, steps and working platforms. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Isolate electricity supply and remove covers from Biodisc unit and check appearance of biomass packs as specified. Visually check the general condition of the plant ensuring that pack retaining fixings are secure. Replace covers and reinstate power supply. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Lift access covers and clean high level alarm float and loss of rotation sensor. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Tidy site. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Visual check on effluent. | 4 | Qtr. | bar: June; Sept; Dec; Mar
Control Kiosk (All equipment must be isolated before any maintenance work is carried out)
| Check cabling, plug-in devices and other fittings and switches. Check heater and thermostat setting. Check operation of instruments, indicators, lamps and security of earthing straps all as specified. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Inspect and clean sample/flow meter chamber by jet washing. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Clean, check operation and oil all padlocks. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Cut the grass and weeds to keep them short and prevent seeding four times per annum (April, June, August and September). Remove cuttings to authorised tip. Strim around fence lines, gates and structures. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Carry out thorough clean of the control kiosk, remove cobwebs and dirt and brush down exterior. | 4 | Qtr. | bar: June; Sept; Dec; Mar
Klargester Biodisc Plant
| Carry out service of Biodisc unit as per Klargester Environmental Engineering’s inspection schedule. | 2 | Biannual | bar: June; Dec
| Check security of fuses, contractors, relays, timers, display instruments and indicator lamps. Check for overheating, burning and freedom of operation all as specified. | 2 | Biannual | bar: June; Dec
| Check soakaway operation. Empty any accumulated effluent/sludge and clean by jet washing. | 1 | Annual | bar: Dec
| After leaf fall in autumn collect all leaves and dispose to authorised tip. Check overhang of trees and report any encroachment over the plant and ancillary structures. | 1 | Annual | bar: Dec
| Weed kill paved areas using an approved weed killer suitable for use adjacent to water courses and above aquifers. | 2 | Biannual | bar: June; Dec

## The Leazes
| STP Somerset - Maintenance Item Description, The Leazes | Quantity | Frequency | Apr | May | June | Jul | Aug | Sept | Oct | Nov | Dec | Jan | Feb | Mar
Item | Maintenance works including:
| Unlock, enter and set telemetry “Engineer on Site” switch. Check security of gates and fences. Check for rodent infestation. Check warning signs, condition of manhole/access covers and frames, ladders, step irons, hand railing, steps and working platforms. | 12 | Monthly | bar: Apr to Mar
| Isolate electricity supply and remove covers from Biodisc unit and check appearance of biomass packs as specified. Visually check the general condition of the plant ensuring that pack retaining fixings are secure. Replace covers and reinstate power supply. | 12 | Monthly | bar: Apr to Mar
| Lift access covers and clean high level alarm float and loss of rotation sensor. | 12 | Monthly | bar: Apr to Mar
| Tidy site. | 12 | Monthly | bar: Apr to Mar
| Visual check on effluent. | 12 | Monthly | bar: Apr to Mar
| Control Kiosk (All equipment must be isolated before any maintenance work is carried out) | 12 | Monthly | bar: Apr to Mar
| Check cabling, plug-in devices and other fittings and switches. Check heater and thermostat setting. Check operation of instruments, indicators, lamps and security of earthing straps all as specified. | 12 | Monthly | bar: Apr to Mar
| Inspect and clean sample/flow meter chamber by jet washing. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Clean, check operation and oil all padlocks. | 12 | Monthly | bar: Apr to Mar
| Cut the grass and weeds to keep them short and prevent seeding four times per annum (April, June, August and September). Remove cuttings to authorised tip. Strim around fence lines, gates and structures. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Carry out thorough clean of the control kiosk, remove cobwebs and dirt and brush down exterior. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Read and record the electricity and water meters (end of June and December). | 2 | Biannual | bar: June; Dec
Klargester Biodisc Plant
| Carry out service of Biodisc unit as per Klargester Environmental Engineering’s inspection schedule. | 2 | Biannual | bar: June; Dec
| Check security of fuses, contractors, relays, timers, display instruments and indicator lamps. Check for overheating, burning and freedom of operation all as specified. | 2 | Biannual | bar: June; Dec

## Zion Hill
| STP Somerset - Maintenance Item Description, Zion Hill | Quantity | Frequency | Apr | May | June | Jul | Aug | Sept | Oct | Nov | Dec | Jan | Feb | Mar
Item | Maintenance works including:
| Unlock, check security of gates and fences. Check for rodent infestation. Check warning signs, condition of manhole covers and frames, ladders, step irons, handrailing and working platforms. | 12 | Monthly | bar: Apr to Mar
| Lift access covers and clean channels, weirs, scum boards and dip pipes of inlet chamber, settlement tank and humus tank by jet washing. Replace covers. | 12 | Monthly | bar: Apr to Mar
| Tidy site. | 12 | Monthly | bar: Apr to Mar
| Visual check on effluent. | 12 | Monthly | bar: Apr to Mar
| Ensure filter vents are clear of obstructions. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Clean all manholes and collection pits within the site by jet washing including channels; walls, benchings and frame rebates. Clean covers and clean lifting eyes of debris and refit | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Clean and check operation and oil padlocks on site. | 12 | Monthly | bar: Apr to Mar
| Service tilting tray | 4 | Qtr. | bar: June; Sept; Dec; Mar
| After leaf fall in autumn collect all leaves and dispose to authorised tip. Check overhang of trees and report any encroachment over the treatment units. | 1 | Annual | bar: Dec
| Weed kill gravelled areas using an approved weed killer suitable for use adjacent to water-courses and above aquifers. | 2 | Biannual | bar: June; Dec

## Ford Close
| STP Cornwall - Maintenance Item Description, Ford Close | Quantity | Frequency | Apr | May | June | Jul | Aug | Sept | Oct | Nov | Dec | Jan | Feb | Mar
Item | Maintenance works including: | To be reviewed post major planned replacement works installation
Unlock, enter and set telemetry “Engineer on Site” switch. Check security of gates and fences. Check for rodent infestation. Check warning signs, condition of manhole/access covers and frames, ladders, step irons, handrailing, steps and working platforms.
Lift access cover and clean high-level alarm float of rags and other debris. Replace cover.
Tidy site.
Visual check on effluent.
SAF Unit and Final Tank Inspect/adjust air pattern as specified.
Blower/Control Kiosk Check reading on pressure gauge as specified.
Blower/Control Kiosk (iv) Check pressure relief for escaping air as specified.
Inspect installation and change bag when blinded or one third full and dispose to authorised tip. Clean frame and fit new bag.
Blower/Control Kiosk
(All equipment must be isolated before any maintenance work is carried out)
Inspect cables and fittings. Check heater and thermostat setting. Check operation of indicators, lamps, light and security of earthing straps.
Check/reset overloads as specified.
Check operation of break tank valve, ball valve and drain down.
Inspect and clean sample/flow meter chamber by jet washing. Remove accumulated debris behind ‘V’ notch weir.
Clean all manholes and collection pits within the site by jet washing, including channels, walls, benchings and frame rebates. Clean covers and clear lifting eyes and re-fit.
Clean, check operation and oil all padlocks on site.
SAF Unit and Final Tank
Ensure septic tank inlets are clear of blockages/solids build-up by jet washing. De-sludge SAF cells (3 No.) and Final Tank as specified. Re-check inlets during and following de-sludging to ensure free flow into septic tanks is maintained.
Carry out thorough clean of the control kiosk, remove cobwebs and dirt and wipe down exterior.
Carry out thorough clean of the control kiosk, remove cobwebs and dirt and wipe down exterior.
Read and record the electricity and water meters (end of June and December).
Clean leaves & other accumulated debris from the site, sweep paved areas and dispose of all arisings to authorised tip.
Change blower air filters (2 No.) as specified.
Check for earth continuity.

## Colehill Drove
| STP Dorset - Maintenance Item Description, Colehill Drove | Quantity | Frequency | Apr | May | June | Jul | Aug | Sept | Oct | Nov | Dec | Jan | Feb | Mar
Item | Maintenance works including:
| (Unlock. Check security of gates and fences. Check for rodent infestation. Check warning signs, condition of manhole/access covers and frames, ladders, step irons, handrailing, steps and working platforms. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Lift access covers and clean channels, weirs, scum boards and dip pipes of inlet chamber and primary balancing tank by jet washing. Clean high level alarm float of rags and other debris. Replace covers. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Tidy site. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Check final effluent discharge as specified. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Inspect and clean sample/flow meter chamber by jet washing. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Clean, check operation and oil all padlocks on site. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Clean all manholes and collection pits within the site by jet washing including channels, walls, benchings and frame rebates. Clean covers and clear lifting eyes and re-fit. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Read and record the electricity meter quarterly (end of March, June, September and December). | 2 | Biannual | bar: June; Dec
| Clean leaves and other accumulated debris from the site and dispose of all arisings to authorised tip. | 2 | Biannual | bar: June; Dec
| Check condition of headwall at outfall. Clear away any accumulated debris and cut back overgrowth. | 2 | Biannual | bar: June; Dec
| Weed kill gravel areas using an approved weed killer suitable for use adjacent to watercourses and above aquifers. | 2 | Biannual | bar: June; Dec
Clereflo Treatment Plant
(Before carrying out the following maintenance task ensure that the power is off and the mains isolator is padlocked)
| Check operation of the re-circulation pump as specified. | 2 | Biannual | bar: June; Dec
| Check and confirm that there are no leaks from exposed pipework. | 2 | Biannual | bar: June; Dec
| Inspect and clean the re-circulation pump as specified. | 2 | Biannual | bar: June; Dec

## Burgess Field
| STP Dorset - Maintenance Item Description, Burgess Field | Quantity | Frequency | Apr | May | June | Jul | Aug | Sept | Oct | Nov | Dec | Jan | Feb | Mar
Item | Maintenance works including: | To be reviewed post major planned replacement works installation
Unlock, enter and set telemetry “Engineer on Site” switch. Check security of gates and fences. Check for rodent infestation. Check warning signs, condition of manhole/access covers and frames, ladders, step irons, hand railing, steps and working platforms.
Isolate electricity supply and remove covers from Biodisc unit and check appearance of biomass packs as specified. Visually check the general condition of the plant ensuring that pack retaining fixings are secure. Replace covers and reinstate power supply.
Lift access covers and clean high level alarm float and loss of rotation sensor.
Tidy site.
Visual check on effluent.
Control Kiosk (All equipment must be isolated before any maintenance work is carried out)
Check cabling, plug-in devices and other fittings and switches. Check heater and thermostat setting. Check operation of instruments, indicators, lamps and security of earthing straps all as specified.
Inspect and clean sample/flow meter chamber by jet washing.
Clean, check operation and oil all padlocks.
Cut the grass and weeds to keep them short and prevent seeding four times per annum (April, June, August and September). Remove cuttings to authorised tip. Strim around fence lines, gates and structures.
Carry out thorough clean of the control kiosk, remove cobwebs and dirt and brush down exterior.
Read and record the electricity meter quarterly (end of March, June, September and December).
Klargester Biodisc Plant
Carry out service of Biodisc unit as per Klargester Environmental Engineering’s inspection schedule.
Check security of fuses, contractors, relays, timers, display instruments and indicator lamps. Check for overheating, burning and freedom of operation all as specified.
(i) Check soakaway operation. Empty any accumulated effluent/sludge and clean by jet washing
After leaf fall in autumn collect all leaves and dispose to authorised tip. Check overhang of trees and report any encroachment over the plant and ancillary structures.
Weed kill paved areas using an approved weed killer suitable for use adjacent to water courses and above aquifers.
Check all bolted main cable joints for security/overheating. Remove deposits of dust or dirt from inside the control cabinet.

## Newtwon Hill
| STP Dorset - Maintenance Item Description, Newtown Hill | Quantity | Frequency | Apr | May | June | Jul | Aug | Sept | Oct | Nov | Dec | Jan | Feb | Mar
Item | Maintenance works including: | To be reviewed post major planned replacement works installation
Unlock. Check security of gates and fences. Check for rodent infestation. Check warning signs, condition of manhole/access covers and frames, ladders, step irons, handrailing, steps and working platforms.
Lift access covers and clean channels, weirs, scum boards and dip pipes of inlet chamber and primary balancing tank by jet washing. Clean high level alarm float of rags and other debris. Replace covers.
Tidy site.
Clereflo Treatment Plant Check final effluent discharge as specified.
Inspect and clean sample/flow meter chamber by jet washing.
Clean, check operation and oil all padlocks on site.
Clean all manholes and collection pits within the site by jet washing including channels, walls, benchings and frame rebates. Clean covers and clear lifting eyes and re-fit.
Clean leaves and other accumulated debris from the site and dispose of all arisings to authorised tip.
Check condition of headwall at outfall. Clear away any accumulated debris and cut back overgrowth.
Weed kill gravel areas using an approved weed killer suitable for use adjacent to watercourses and above aquifers.
Clereflo Treatment Plant
Check operation of the re-circulation pump as specified.
Check and confirm that there are no leaks from exposed pipework.
(Before carrying out the following maintenance task ensure that the power is off and the mains isolator is padlocked)
Inspect and clean the re-circulation pump as specified.
Read and record the electricity meter (end of June and December).

## Shaggs Cottages
| STP Dorset - Maintenance Item Description, Shaggs cottages | Quantity | Frequency | Apr | May | June | Jul | Aug | Sept | Oct | Nov | Dec | Jan | Feb | Mar
Item | Maintenance works including: | To be reviewed post major planned replacement works installation
Unlock, check security of gates and fences. Check for rodent infestation. Check warning signs, condition of manhole covers and frames, ladders, step irons, handrailing and working platforms.
Lift access covers, inspect and clean distributor arms to ensure filter arms are free of debris and effluent is being evenly distributed. Check for surface ponding and report. Replace covers
Lift access covers and clean channels, weirs, scum boards and dip pipes of inlet chamber, settlement tank and humus tank by jet washing. Replace covers.
Tidy site.
Visual check on effluent.
Service tilting tray
Check quality of final effluent. If cloudy or contains suspended particles rectify as specified.
Ensure filter vents are clear of obstructions.
Clean all manholes and collection pits within the site by jet washing including channels; walls, benchings and frame rebates. Clean covers and clean lifting eyes of debris and refit.
Clean and check operation and oil padlocks on site.
Check filter distribution system generally for wear and tear and report on findings.
Service tilting tray
After leaf fall in autumn collect all leaves and dispose to authorised tip. Check overhang of trees and report any encroachment over the treatment units.
Weed kill gravelled areas using an approved weed killer suitable for use adjacent to water-courses and above aquifers.

## Blackmanston
| STP Dorset - Maintenance Item Description, Blackmanston | Quantity | Frequency | Apr | May | June | Jul | Aug | Sept | Oct | Nov | Dec | Jan | Feb | Mar
Item | Maintenance works including:
| Unlock, check security of gates and fences. Check for rodent infestation. Check warning signs, condition of manhole covers and frames, ladders, step irons, handrailing and working platforms. | 12 | Monthly | bar: Apr to Mar
| Lift access covers, inspect and clean distributor arms to ensure filter arms are free of debris and effluent is being evenly distributed. Check for surface ponding and report. Replace covers | 12 | Monthly | bar: Apr to Mar
| Lift access covers and clean channels, weirs, scum boards and dip pipes of inlet chamber, settlement tank and humus tank by jet washing. Replace covers. | 12 | Monthly | bar: Apr to Mar
| Tidy site. | 12 | Monthly | bar: Apr to Mar
| Visual check on effluent. | 12 | Monthly | bar: Apr to Mar
| Check quality of final effluent. If cloudy or contains suspended particles rectify as specified. | 12 | Monthly | bar: Apr to Mar
| Ensure filter vents are clear of obstructions. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Clean all manholes and collection pits within the site by jet washing including channels; walls, benchings and frame rebates. Clean covers and clean lifting eyes of debris and refit. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Clean and check operation and oil padlocks on site. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Service tilting tray | 2 | Biannual | bar: June; Dec
| After leaf fall in autumn collect all leaves and dispose to authorised tip. Check overhang of trees and report any encroachment over the treatment units. | 1 | Annual | bar: Dec
| Weed kill gravelled areas using an approved weed killer suitable for use adjacent to water-courses and above aquifers. | 1 | Annual | bar: Dec

## Woodford Lane
| STP Dorset - Maintenance Item Description, Woodford Lane | Quantity | Frequency | Apr | May | June | Jul | Aug | Sept | Oct | Nov | Dec | Jan | Feb | Mar
Item | Maintenance works including:
| Unlock, check security of gates and fences. Check for rodent infestation. Check warning signs, condition of manhole covers and frames, ladders, step irons, handrailing and working platforms. | 12 | Monthly | bar: Apr to Mar
| Lift access covers, inspect and clean distributor arms to ensure filter arms are free of debris and effluent is being evenly distributed. Check for surface ponding and report. Replace covers | 12 | Monthly | bar: Apr to Mar
| Lift access covers and clean channels, weirs, scum boards and dip pipes of inlet chamber, settlement tank and humus tank by jet washing. Replace covers. | 12 | Monthly | bar: Apr to Mar
| Tidy site. | 12 | Monthly | bar: Apr to Mar
| Visual check on effluent. | 12 | Monthly | bar: Apr to Mar
| Ensure filter vents are clear of obstructions. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Clean all manholes and collection pits within the site by jet washing including channels; walls, benchings and frame rebates. Clean covers and clean lifting eyes of debris and refit. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Clean and check operation and oil padlocks on site. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Service tilting tray | 2 | Biannual | bar: June; Dec
| After leaf fall in autumn collect all leaves and dispose to authorised tip. Check overhang of trees and report any encroachment over the treatment units. | 1 | Annual | bar: Dec
| Weed kill gravelled areas using an approved weed killer suitable for use adjacent to water-courses and above aquifers. | 1 | Annual | bar: Dec

## Organford
| STP Dorset - Maintenance Item Description, Organford | Quantity | Frequency | Apr | May | June | Jul | Aug | Sept | Oct | Nov | Dec | Jan | Feb | Mar
Item | Maintenance works including:
| Unlock. Check security of gates and fences. Check for rodent infestation. Check warning signs, condition of manhole/access covers and frames, ladders, step irons, handrailing, steps and working platforms. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Lift access covers and clean channels, weirs, scum boards and dip pipes of inlet chamber and primary balancing tank by jet washing. Clean high level alarm float of rags and other debris. Replace covers. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Tidy site. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Clean all manholes and collection pits within the site by jet washing including channels, walls, benchings and frame rebates. Clean covers and clear lifting eyes and re-fit. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Inspect and clean sample/flow meter chamber by jet washing. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Clean, check operation and oil all padlocks on site. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Read and record the electricity meter(end of June and December). | 2 | Biannual | bar: June; Dec
| Clean leaves and other accumulated debris from the site and dispose of all arisings to authorised tip. | 2 | Biannual | bar: June; Dec
| Check condition of headwall at outfall. Clear away any accumulated debris and cut back overgrowth. | 2 | Biannual | bar: June; Dec
| Weed kill gravel areas using an approved weed killer suitable for use adjacent to watercourses and above aquifers. | 2 | Biannual | bar: June; Dec
Clereflo Treatment Plant
(Before carrying out the following maintenance task ensure that the power is off and the mains isolator is padlocked)
| Check operation of the re-circulation pump as specified. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Check and confirm that there are no leaks from exposed pipework. | 4 | Qtr. | bar: June; Sept; Dec; Mar
| Check final effluent discharge as specified. | 2 | Biannual | bar: June; Dec
| Inspect and clean the re-circulation pump as specified. | 4 | Qtr. | bar: June; Sept; Dec; Mar